## Input
|  |  | 1-Line 2011 Version 11.0A - Copyright Durand & Associates |  |  |  |  | 0
Main Switch Board | [8 empty] | 99 | [33 empty] | 15 | [5 empty] | 99
|  | CODE YEAR | 2011 | [24 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS01 | 100A | [8 empty] | 20 |  | 0 |  | ERROR | MANUAL |  | MANUAL | PANEL | XMFR
General Information |  |  |  |  | Circuit Loads |  |  | 0 |  |  |  |  | Error Check | [14 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS02 | 100A |  |  | 60 | 60 |  |  |  |  | 25 |  |  |  |  | ERROR | UPDATE | FEEDER | ERROR | ERROR
[16 empty] | Number of Circuits |  | STANDARD | [9 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS03 | 100A |  |  | 60 | 70 |  |  |  |  | 30 | [6 empty] | ERROR
| PANEL NAME |  | MAIN SWITCHBOARD |  |  | C1 | PANEL |  | PANEL NAME | MAIN SWITCHBOARD |  |  | P1 | 0 | C1 | 1 | TRUE | BREAKER |  | PANEL NAME | 0 |  |  | 0 |  |  |  | 100 | A | 100A | SPACE | 100A SPACE | SAMPS04 | 100A |  |  | 70 | 80 |  |  |  |  | 35 |  | P1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
| FED FROM |  | SERVICE |  |  | C2 | PANEL |  | FED FROM | SERVICE |  |  | P2 | 0 | C2 | 1 | TRUE |  |  | FED FROM | [7 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS05 | 100A |  |  | 80 | 90 |  |  |  |  | 40 |  | P2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
| # OF CIRCUITS |  | 4 |  |  | C3 | XMFR |  | # OF CIRCUITS | 4 |  |  | P3 | 0 | C3 | 1 | TRUE | 60 |  | # OF CIRCUITS | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS06 | 100A |  |  | 90 | 100 |  |  |  |  | 45 |  | P3 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
| HIGH VOLTAGE |  | 480 |  |  | C4 | MANUAL |  | HIGH VOLTAGE | 480 |  |  | P4 | 0 | C4 | 1 | TRUE | 70 |  | HIGH VOLTAGE | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS07 | 100A |  |  | 100 | 110 |  |  |  |  | 50 |  | P4 | 0 | 0 | 0 | 1 | 0 |  |  | 0
| LOW VOLTAGE |  | 277 | ALL CELLS ARE PROTECTED |  |  | XMFR |  | LOW VOLTAGE | 277 |  |  | P5 | 0 | C5 | 0 | TRUE | 80 |  | LOW VOLTAGE | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS08 | 100A |  |  | 110 | 125 |  |  |  |  | 60 |  | P5 | 0 | 0 | 0 | 1 | 0
| PHASE |  | 3Y | IN THIS DEMO VERSION |  |  | XMFR |  | PHASE | 3Y |  |  | P6 | 0 | C6 | 0 | TRUE | 90 |  | PHASE | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS09 | 100A |  |  | 125 | 150 |  |  |  |  | 70 |  | P6 | 0 | 0 | 0 | 1 | 0
|  |  | AUTO |  |  |  | XMFR |  | HI-LEG SIZE (L2) | AUTO |  |  | P7 | 0 | C7 | 0 | TRUE | 100 |  | HI-LEG SIZE | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS10 | 100A |  |  | 150 | 175 |  |  |  |  | 80 |  | P7 | 0 | 0 | 0 | 1 | 0
| NEUTRAL SIZE |  | AUTO |  |  |  | XMFR |  | NEUTRAL SIZE | AUTO |  |  | P8 | 0 | C8 | 0 | TRUE | 110 |  | NEUTRAL | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS11 | 100A |  |  | 175 | 200 |  |  |  |  | 90 |  | P8 | 0 | 0 | 0 | 1 | 0
| HERTZ |  | 60 |  |  |  | XMFR |  | HERTZ | 60 |  |  | P9 | 0 | C9 | 0 | TRUE | 125 |  | HERTZ | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS12 | 100A |  |  | 200 | 225 |  |  |  |  | 100 |  | P9 | 0 | 0 | 0 | 1 | 0
| MIN AMPS |  | 0 |  |  |  | XMFR |  | MIN AMPS | 0 |  |  | P10 | 0 | C10 | 0 | TRUE | 150 |  | MIN AMPS | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS13 | 100A |  |  | 225 | 250 |  |  |  |  | 110 |  | P10 | 0 | 0 | 0 | 1 | 0
|  |  | 0 |  |  |  | XMFR |  | MIN AMPS (L2) | 0 |  |  | P11 | 0 | C11 | 0 | TRUE | 175 |  | MIN AMPS (L2) | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS14 | 100A |  |  | 250 | 300 |  |  |  |  | 125 |  | P11 | 0 | 0 | 0 | 1 | 0
| MIN AMPS NEUTRAL |  | 0 |  |  |  | XMFR |  | MIN AMPS NEUTRAL | 0 |  |  | P12 | 0 | C12 | 0 | TRUE | 200 |  | MIN AMPS NEUTRAL | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS15 | 100A |  |  | 300 | 350 |  |  |  |  | 150 |  | P12 | 0 | 0 | 0 | 1 | 0
| % FACTOR |  | 0 |  |  |  | XMFR |  | % FACTOR | 0 |  |  | P13 | 0 | C13 | 0 | TRUE | 225 |  | % FACTOR | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS16 | 100A |  |  | 350 | 400 |  |  |  |  | 175 |  | P13 | 0 | 0 | 0 | 1 | 0
|  |  | 20 |  |  |  | XMFR |  | % FACTOR (L2) | 20 |  |  | P14 | 0 | C14 | 0 | TRUE | 250 |  | % FACTOR (L2) | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS17 | 100A |  |  | 400 | 450 |  |  |  |  | 200 |  | P14 | 0 | 0 | 0 | 1 | 0
| MAIN BREAKER SIZING |  | AUTO |  |  |  | PANEL |  | DISTANCE TO ATS | 15 |  |  | P15 | 0 | C15 | 0 | TRUE | 300 |  | MAIN BREAKER SIZING | 0 | << SELECT METHOD |  |  | 0 |  |  | 100 | A | 100A | SPACE | 100A SPACE | SAMPS18 | 100A |  |  | 450 | 500 |  |  |  |  | 225 |  | P15 | 0 | 0 | 0 | 1 | 0
|  |  | 4000 |  |  |  | PANEL | [5 empty] | P16 | 0 | C16 | 0 | TRUE | 350 |  | ENTER MAIN BREAKER AMPS | 0 | << SELECT AMPS | [5 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS19 | 100A |  |  | 500 | 600 |  |  |  |  | 250 |  | P16 | 0 | 0 | 0 | 1 | 0
[7 empty] | PANEL | [5 empty] | P17 | 0 | C17 | 0 | TRUE | 400 | [9 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS20 | 100A |  |  | 600 | 700 |  |  |  |  | 300 |  | P17 | 0 | 0 | 0 | 1 | 0
[7 empty] | MANUAL | [5 empty] | P18 | 0 | C18 | 0 | TRUE | 450 | [9 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS21 | 100A |  |  | 700 | 800 |  |  |  |  | 350 |  | P18 | 0 | 0 | 0 | 1 | 0 |  |  | 0
1-Line Display Options | [6 empty] | MANUAL |  | MAIN BREAKER | 1 |  |  | P19 | 0 | C19 | 0 | TRUE | 500 |  | MAIN BREAKER | 0 | << ENTER YES or NO | [5 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS22 | 100A |  |  | 800 | 1000 |  |  |  |  | 400 |  | P19 | 0 | 0 | 0 | 1 | 0 |  |  | 0
[7 empty] | SPACE |  | METER | 1 |  |  | P20 | 0 | C20 | 0 | FALSE | 600 |  | METER | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS23 | 100A |  |  | 1000 | 1200 |  |  |  |  | 450 |  | P20 | 0 | 0 | 0 | 1 | 0 |  |  | 0
| SHOW MAIN METER |  | YES |  |  |  | SPACE |  | SHOW AFC | 0 |  |  | P21 | 0 | C21 | 0 | FALSE | 700 |  | SHOW FAULT CURRENT | 0 | [6 empty] | 100 | A | 100A | SPACE | 100A SPACE | SAMPS24 | 100A |  |  | 1200 | 1600 |  |  |  |  | 500 |  | P21 | 0 | 0 | 0 | 1 | 0 |  |  | 0
| SHOW CURRENT TRANSFORMER |  | YES |  |  |  | PANEL |  | SHOW VD | 1 |  |  | P22 | 0 | C22 | 0 | TRUE | 800 |  | SHOW VOLTAGE DROP | 0 | [15 empty] | 1600 | 2000 |  |  |  |  | 600 |  | P22 | 0 | 0 | 0 | 1 | 0
| SHOW FAULT CURRENT |  | YES | ALL CELLS ARE PROTECTED |  |  | PANEL | FALSE | SHOW LENGTH | 1 |  |  | P23 | 0 | C23 | 0 | TRUE | 1000 |  | SHOW CONDUIT LENGTH | 0 | [15 empty] | 2000 | 2500 |  |  |  |  | 700 |  | P23 | 0 | 0 | 0 | 1 | 0
| SHOW VOLTAGE DROP % |  | YES | IN THIS DEMO VERSION |  |  | PANEL |  | SHOW SYS GND | 1 |  |  | P24 | 0 | C24 | 0 | TRUE | 1200 |  | SHOW SYSTEM GROUND | 0 | [15 empty] | 2500 | 3000 |  |  |  |  | 800 |  | P24 | 0 | 0 | 0 | 1 | 0
| SHOW CONDUIT LENGTH |  | YES | [5 empty] | SHOW TRUE | 1 | [7 empty] | 1600 |  | MUST BE THE SAME | 0 | << MUST BE THE SAME --------------------- | [5 empty] | 4000 | A | 4000A | [6 empty] | 3000 | 4000 |  |  |  |  | 1000
| SHOW UFER GROUND |  | YES | [14 empty] | 2000 |  | AUTO NA | 0 | [15 empty] | 4000 | 5000 |  |  |  |  | 1200
| SHOW TRUE PHASE CONNECTION |  | YES |  | Spare or Space Size Amps | [12 empty] | 2500 |  | GENSET DIST | 0 | [13 empty] | 327.6 |  | 5000 | 6000 |  |  |  |  | 1600 |  |  | 0 | 0
[18 empty] | 3000 |  | CODE YEAR | 0 | [21 empty] | 2000
[7 empty] | 100 |  | MAX LOAD | 327.6 | [7 empty] | 4000 |  | AUTO SIZING | 0 | << ENTER YES or NO | [14 empty] | 350 | [5 empty] | 2500
Service Entrance Feeder Options | [6 empty] | 100 |  | NONE | [8 empty] | 5000 | [24 empty] | 3000
[7 empty] | 100 |  | UTILITY TRANSFORMER INFINITE BUS | [8 empty] | 6000 |  | WIRE TYPE | 0 | [15 empty] | 350 | [5 empty] | 4000
| SERVICE FEEDER SIZING |  | AUTO |  |  |  | 100 |  | TRANSFORMER KNOWN AFC | [10 empty] | WIRE CU/AL? | 0 | 0 | 0 | [19 empty] | 5000
| WIRE TYPE |  | THHN |  |  |  | 100 |  | NO TRANSFORMER KNOWN AFC |  |  |  | Master Error | 0 | [5 empty] | WIRE TEMP C | 0 | [21 empty] | 6000
| WIRE CU/AL |  | CU |  |  |  | 100 | [12 empty] | WIRE LENGTH | 0 | [6 empty] | CU
| WIRE TEMP C |  | 75 |  |  |  | 100 | [12 empty] | CONDUIT TYPE | 0 |  | 0
| WIRE LENGTH |  | 100 |  |  |  | 100 | [12 empty] | OVERHEAD \ UNDERGROUND | 0 | [6 empty] | 225 Amp
| CONDUIT TYPE |  | RIGID |  |  |  | 100 |  |  | 3000 A |  | 3000 A | [7 empty] | CONDUIT / BUSWAY | 0 | [6 empty] | 400 Amp
| OVERHEAD \ UNDERGROUND |  | OVERHEAD |  |  |  | 100 |  |  | 1 | - | #500 |  | THHN |  | CU | 1-#500 THHN CU |  |  | CONDUIT/BUSWAY LENGTH | 0 | [6 empty] | 600 Amp
|  |  | CONDUIT |  |  |  | 100 |  |  | CONDUIT |  | CONDUIT | [7 empty] | CONDUIT SIZE | 0 | [6 empty] | 800 Amp
|  |  | 30 |  |  |  | 100 |  |  | 1 | - | 4" |  | EMT |  | 1-4" EMT |  |  |  | BUSWAY SIZE | 0 | << SELECT SIZE | [5 empty] | 1000 Amp
|  |  | 4" |  |  |  | 100 | [12 empty] | # OF CONDUSTORS PER PHASE | 0 | << ENTER # OF CONDUCTORS | [5 empty] | 1200 Amp
|  |  | 3000 A | ALL CELLS ARE PROTECTED |  |  | 100 | [6 empty] | 5 | #6 | 0 | 0 | 1 |  | WIRE CU/AL | 0 | [6 empty] | 1350 Amp
|  |  |  | IN THIS DEMO VERSION |  |  | 100 | [6 empty] | 6 | #4 | 0 | 0 | 0 |  | WIRE TYPE | 0 |  | 0 |  |  |  |  | 1600 Amp
|  |  | CU |  |  |  | 100 | [6 empty] | 7 | #3 | 0 | 0 | 0 |  | WIRE SIZE | 0 | [6 empty] | 2000 Amp
|  |  | THHN |  |  |  | 100 |  | FALSE |  |  |  |  | 8 | #2 | 0 | 0 | 0 |  | WIRE SIZE (HI-LEG L2) | 0
|  |  | #500 |  |  |  | 100 | [6 empty] | 9 | #1 | 0 | 0 | 0 |  | NEUTRAL SIZE | 0 | [6 empty] | 2500 Amp
|  |  | #6 |  |  |  | 100 | TRUE | [5 empty] | 10 | #1/0 | 0 | 0 | 0 |  | CONDUIT TYPE | 0 |  | 0 |  |  |  |  | 3000 Amp
|  |  | #500 |  |  |  | 100 | [6 empty] | 11 | #2/0 | 0 | 0 | 0 |  | ATS YES/NO | 0 | [6 empty] | 4000 Amp
|  |  | EMT |  |  |  | 100 | [6 empty] | 12 | #3/0 | 0 | 0 | 0 |  | ATS SIZING | 0
|  |  | 1 |  |  |  | 100 | [6 empty] | 13 | #4/0 | 0 | 0 | 0 |  | ATS MANUAL SIZE | 0
[7 empty] | 100 |  | NONE |  | 0 |  |  | 14 | #250 | 0 | 0 | 0 |  | DIS FROM MSWBD | 0
[7 empty] | 100 |  | UTILITY XMFR AUTO/NONE |  | 0 |  |  | 15 | #300 | 0 | 0 | 0 |  | SELECT METHOD | 0 |  |  | 0 | FALSE
Fault Current Calculations for Incoming Power | [8 empty] | UTILITY XMFR MANUAL |  | 0 |  |  | 16 | #350 | 0 | 0 | 0 |  | AVAILABLE FAULT CURRENT | 0
[9 empty] | XMFR KNOWN AFC AUTO |  | 0 |  |  | 17 | #400 | 0 | 0 | 0 |  | UTILITY VOLTAGE ADJUSTMENT | 0 | [17 empty] | GENERATOR GROUNDING ELECTRODE
| SELECT METHOD |  | NO TRANSFORMER KNOWN AFC | [5 empty] | XMFR KNOWN AFC MANUAL |  | 0 |  |  | 18 | #500 | 1 | 1 | 0 |  | TRANSFORMER KVA | 0 | [6 empty] | MOTOR START
| AVAILABLE FAULT CURRENT |  | 44903 | [5 empty] | NO XMFR KNOWN AFC AUTO |  | 5 |  |  | 19 | #600 | 0 | 0 | 0 |  | TRANSFORMER %Z RATING | 0 | [6 empty] | LOAD |  | VA | VOLTS | PHASE | [6 empty] | WIRE SIZE | #1/0
| UTILITY VOLTAGE ADJUSTMENT |  | 1 | [5 empty] | NO XMFR KNOWN AFC MANUAL |  | 0 |  |  | 20 | #750 | 0 | 0 | 0 |  | PRIMARY VOLTAGE | 0 |  |  | P1 SIZE | 180 |  |  | 39000 | P1 SIZE | 149455 | 480 | 3Y | 1.732 | 180 |  | 110455 |  |  | # WIRES | 1 | - | #6 | GND | 1-#6 GND
|  |  | 500 | [10 empty] | 21 | #1000 | 0 | 0 | 0 |  | GENSET YES NO | 0 |  |  | X1 SIZE |  |  |  | 0 | X1 SIZE | [9 empty] | CU/AL | CU
|  |  | 3 | [5 empty] | 150 | KW | 150 KW |  |  |  |  | 1 | 1 | 1 |  | GENSET SIZING | 0 |  |  | MANUAL SIZE |  |  |  |  | MANUAL SIZE | 0 | [5 empty] | 39000
|  |  | 13200 | [16 empty] | GEN KW | 0 | [14 empty] | 0 |  |  |  | WIRE | GND SIZE
[20 empty] | SPACE/SPARE 1 | 0 |  |  | MAX | 180 |  |  |  |  | 149 | KW | 149 KW |  |  |  | 110455 |  |  |  | SIZE |  |  |  | CONDUCTOR
[11 empty] | 5 | [8 empty] | SPACE/SPARE 2 | 0 |  |  | MANUAL | 200 |  |  |  |  | 149.455 | [5 empty] | 39000 |  |  | #1/0 | #6 | 5 | 0 | SYSTEM GROUND | SIZE CODE | 10 |  | #6
Automatic Transfer Switch & Engine Generator ( Located at Circuit Position C1 ) | [19 empty] | SPACE/SPARE 3 | 0 |  |  |  | 0 | [10 empty] | 149455 |  |  | #1/0 | #4 | 6 | 0 |  | CU | 1 |  | #6
[9 empty] | 15 | ' | 15' | [8 empty] | SPACE/SPARE 4 | 0 | [17 empty] | #1/0 | #3 | 7 | 0
| AUTOTRANSFERSWITCH |  | YES | [5 empty] | 25 | ' | 25' | [8 empty] | SPACE/SPARE 5 | 0 |  |  | << MIN SIZE IS | 180 | A | << MIN SIZE IS 180A |  | P1 SIZE | 1 |  | AUTO | 3Y | [5 empty] | #1/0 | #2 | 8 | 0 |  | WIRE | WIRE | SYS
| TRANSFER SWITCH SIZING |  | MANUAL | [7 empty] | CU | [8 empty] | SPACE/SPARE 6 | 0 | [7 empty] | X1 SIZE | 0 | [8 empty] | #1/0 | #1 | 9 | 0 |  | SIZE | SIZE | GND
| SIZE OF TRANSFER SWITCH (AMPS) |  | 200 | [16 empty] | SPACE/SPARE 7 | 0 | [7 empty] | MANUAL SIZE | 0 | [8 empty] | #1/0 | #1/0 | 10 | 10 |  | CODE | AWG | SIZE
| ATS DISTANCE FROM MSWBD |  | 15 | ALL CELLS ARE PROTECTED |  |  |  |  | 0 | 0 | 225 A | 225 |  | 0 | 1" |  |  |  |  | SPACE/SPARE 8 | 0 | [11 empty] | 3Y | [5 empty] | #1/0 | #2/0 | 11 | 0 |  | 5 | #6 | #8
| ENGINE GENERATOR |  | YES | IN THIS DEMO VERSION |  |  |  |  | 0 | 0 | 400 A | 400 |  | 0 | 1 1/4" |  |  |  |  | SPACE/SPARE 9 | 0 | [8 empty] | 1 | 480 | / | 277 | V - | 3-PHASE WYE | 480/277V - 3-PHASE WYE |  |  | #1/0 | #3/0 | 12 | 0 |  | 6 | #4 | #8
| GENERATOR SIZING |  | MANUAL | [5 empty] | 0 | 0 | 600 A | 600 |  | 0 | 1 1/2" |  |  |  |  | SPACE/SPARE 10 | 0 | [17 empty] | #1/0 | #4/0 | 13 | 0 |  | 7 | #3 | #8
| KW OF GENERATOR |  | 150 | [5 empty] | 0 | 0 | 800 A | 800 |  | 0 | 2" |  |  |  |  | SPACE/SPARE 11 | 0 | [17 empty] | #1/0 | #250 | 14 | 0 |  | 8 | #2 | #8
| GEN-SET DISTANCE FROM ATS |  | 25 | [5 empty] | 0 | 0 | 1000 A | 1000 |  | 0 | 2 1/2" |  |  |  |  | SPACE/SPARE 12 | 0 | [17 empty] | #1/0 | #300 | 15 | 0 |  | 9 | #1 | #6
[9 empty] | 0 | 0 | 1200 A | 1200 |  | 0 | 3" |  |  |  |  | SPACE/SPARE 13 | 0 | [17 empty] | #1/0 | #350 | 16 | 0 |  | 10 | #1/0 | #6
[9 empty] | 0 | 0 | 1350 A | 1350 |  | 0 | 3 1/2" |  |  |  |  | SPACE/SPARE 14 | 0 | [7 empty] | 149 | KW | [8 empty] | #1/0 | #400 | 17 | 0 |  | 11 | #2/0 | #4
|  |  | 1-Line 2011 Version 11.0A - Copyright Durand & Associates | [5 empty] | 0 | 0 | 1600 A | 1600 |  | 1 | 4" |  |  |  |  | SPACE/SPARE 15 | 0 | [7 empty] | 150 | [9 empty] | #1/0 | #500 | 18 | 0 |  | 12 | #3/0 | #4
[9 empty] | 0 | 0 | 2000 A | 2000 |  | 0 | 5" |  |  |  |  | SPACE/SPARE 16 | 0 | [7 empty] | 0 | [12 empty] | 10 |  | 13 | #4/0 | #2
[9 empty] | 0 | 0 | 2500 A | 2500 |  | 0 | 6" |  |  |  |  | SPACE/SPARE 17 | 0 | [22 empty] | 14 | #250 | #2
[9 empty] | 3000 | 1 | 3000 A | 3000 | [7 empty] | SPACE/SPARE 18 | 0 |  |  | << MIN SIZE IS | 149 |  | KW | << MIN SIZE IS 149 KW | [15 empty] | 15 | #300 | #2
[9 empty] | 0 | 0 | 4000 A | 4000 | [7 empty] | SPACE/SPARE 19 | 0 | [22 empty] | 16 | #350 | #2
[14 empty] | 1 | [5 empty] | SPACE/SPARE 20 | 0 |  |  |  | 180 | [18 empty] | 17 | #400 | #1/0
[9 empty] | 3000 | 1 | [9 empty] | SPACE/SPARE 21 | 0 | [22 empty] | 18 | #500 | #1/0
[9 empty] | 327.6 | [10 empty] | SPACE/SPARE 22 | 0 |  |  |  | 0 | 60
[9 empty] | 0 | [10 empty] | SPACE/SPARE 23 | 0 |  |  |  | 60 | 100 | [17 empty] | WIRE AMPS | 150 | WIRE TEMP | 75
[20 empty] | SPACE/SPARE 24 | 0 |  |  |  | 100 | 150 | [19 empty] | 75 C | 60º C | GROUND | 75 C | 90º C | WIRE
[20 empty] | # CONDUITS | 0 |  |  |  | 150 | 200 | [19 empty] | AMPS | AMPS | WIRE | AMPS | AMPS | SIZE
[21 empty] | 0 |  |  |  | 200 | 300 | [19 empty] | CU | CU | SIZE | CU | CU | AWG
[25 empty] | 300 | 400 | [18 empty] | 0 | 420 | 355 | #1/0 | 420 | 475 | #600
[25 empty] | 400 | 600 | [18 empty] | 420.001 | 460 | 385 | #2/0 | 460 | 520 | #700
[25 empty] | 600 | 800 | [18 empty] | 460.001 | 475 | 400 | #2/0 | 475 | 535 | #750
[10 empty] | WIRE | WIRE | SYSTEM |  | AUTO | #400 | 14 | #4 | 1 | [6 empty] | 800 | 1000 | [18 empty] | 475.001 | 490 | 410 | #2/0 | 490 | 555 | #800
[10 empty] | SIZE | SIZE | GROUND |  | MANUAL | #500 | 15 | #4 | 2 | [6 empty] | 1000 | 1200 | [18 empty] | 490.001 | 520 | 435 | #2/0 | 520 | 585 | #900
[10 empty] | AWG | CODE |  |  | BUSWAY |  |  | #4 | 3 | [26 empty] | 520.001 | 545 | 455 | #2/0 | 545 | 615 | #1000
[9 empty] | 1 | #6 | 5 | #8 | [10 empty] | AUTO ATS SIZE | 200 |  | P1 SIZE | 3Y | 3 | [16 empty] | 545.001 | 590 | 495 | #3/0 | 590 | 665 | #1250
[9 empty] | 2 | #4 | 6 | #8 | [10 empty] | MANUAL ATS SIZE | 200 |  | X1 SIZE |  | 0 | [16 empty] | 590.001 | 625 | 520 | #3/0 | 625 | 705 | #1500
[9 empty] | 3 | #3 | 6 | #8 | [10 empty] | ATS SIZE | 200 |  | MANUAL SIZE |  | 0 | [16 empty] | 625.001 | 650 | 545 | #3/0 | 650 | 735 | #1750
[9 empty] | 4 | #2 | 8 | #8 |  |  |  |  | #4 | 1 | [9 empty] | 3 | [16 empty] | 650.001 | 665 | 560 | #3/0 | 665 | 750 | #2000
[9 empty] | 5 | #1 | 9 | #6 |  |  |  |  | CU | [6 empty] | 200 | A- |  |  | 3P |  | 200A-3P
[9 empty] | 6 | #1/0 | 10 | #6 | [11 empty] | 200 | A |  |  |  |  | 200A | [14 empty] | #1/0
[9 empty] | 7 | #2/0 | 11 | #6 |  |  |  |  | #4 CU
[9 empty] | 8 | #3/0 | 12 | #4
[9 empty] | 9 | #3/0 | 12 | #4
[9 empty] | 10 | #4/0 | 12 | #4
[9 empty] | 11 | #250 | 12 | #4
[9 empty] | 12 | #300 | 12 | #4
[9 empty] | 13 | #350 | 12 | #4 | [14 empty] | -
[9 empty] | 14 | #400 | 12 | #4 | [14 empty] | -
[9 empty] | 15 | #500 | 12 | #4 | [14 empty] | -
[9 empty] | 16 | #600 | 12 | #4 | [14 empty] | -
[9 empty] | 17 | #750 | 12 | #4 | [14 empty] | -
[9 empty] | 18 | #1000 | 12 | #4
AUTO
[10 empty] | LENGTH | 100 | ' | [6 empty] | 1 | 100'
[10 empty] | CONDUIT | 1 | - | 3'' |  | RIGID |  | CU |  | 2 | 1-3'' RIGID
[10 empty] | WIRE 1 | [8 empty] | 3 | 4-#400 THHN CU
[10 empty] | WIRE 2 | [8 empty] | 4
[10 empty] | WIRE 3 | [8 empty] | 5
WIRE 4
3Y
MANUAL
[10 empty] | LENGTH | 30 | ' | [6 empty] | 1 | 30' |  | 30'
[10 empty] | CONDUIT | 1 | - | 4" |  | EMT |  |  |  | 2 | 1-4" EMT |  | 1-4" EMT
[10 empty] | WIRE 1 | 3 | - | #500 |  | THHN |  | CU |  | (L1, L2, L3) | 3-#500 THHN CU (L1, L2, L3) |  | 3-#500 THHN CU (L1, L2, L3)
[10 empty] | WIRE 2 | 1 | - | #6 |  | THHN |  | CU |  | 99 |  |  | 1-#500 THHN CU (N)
[10 empty] | WIRE 3 | 1 | - | #500 |  | THHN |  | CU |  | (N) | 1-#500 THHN CU (N)
[11 empty] | L1 | L2 | L3 | N | SUM | MAX 1 | MAX 2 | MAX 3 | 1 | 100'
[19 empty] | 2 | 1-3'' RIGID
[9 empty] | 5 | #6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4-#400 THHN CU
[9 empty] | 6 | #4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4
[9 empty] | 7 | #3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5
[9 empty] | 8 | #2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 9 | #1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 10 | #1/0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 11 | #2/0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 12 | #3/0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 13 | #4/0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 14 | #250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 15 | #300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 16 | #350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 17 | #400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 18 | #500 | 1 | 1 | 1 | 1 | 4 | 18 | 0 | 0
[9 empty] | 19 | #600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 20 | #750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 21 | #1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 18 | 0 | 0
[10 empty] | 4 | - | #500
[10 empty] | #N/A | - | #N/A
[10 empty] | #N/A | - | #N/A
[10 empty] | 4 |  | #500
[10 empty] | 3000 A |  |  |  | 3000 A
[10 empty] | CU |  | BUSWAY |  | CU BUSWAY

## M Loads
[40 empty] | FALSE | [24 empty] | AUTO
Manual Loads Imput | [31 empty] | AUTO | [34 empty] | ERROR CHECK | [36 empty] | CONNECTED |  | VOLTS | PHASE | AMPS
[5 empty] | BREAKER | (L2) HI-LEG |  | VA |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  | # OF |  |  |  |  | 3Y | [7 empty] | VA |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  | # OF |  | VA | [5 empty] | FUSE | [28 empty] | MAX | MAX X3 | VOLTS | PHASE | AMPS | AMPS X4 | MAX LOAD | MAX X3
CIR | DESCRIPTION | SYMBOL | PHASE | BREAKER | OR FUSE | FUSE |  | CONNECTED LOAD |  |  | GENERAL LOAD |  |  | RECEPTACLE LOAD |  |  | CONTINUOUS LOAD |  |  | MOTOR LOAD |  |  | LARGEST MOTOR LOAD |  |  | KITCHEN LOAD |  | KITCHEN | [8 empty] | BREAKER |  | BREAKER |  | CONNECTED LOAD |  |  | GENERAL LOAD |  |  | RECEPTACLE LOAD |  |  | CONTONUOUS LOAD |  |  | MOTOR LOAD |  |  | LARGEST MOTOR |  |  | KITCHEN LOAD |  | KITCHEN |  | NEUTRAL LOAD |  |  |  |  | 3Y | BREAKER
| OF LOAD |  |  | OR FUSE | AMPS | AMPS | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | CIRCUITS | [8 empty] | AMPS |  | AMPS | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | CIRCUITS | L1 | L2 | L3
1 | LOAD 1 | COMBO STARTER | 1 | BREAKER | 15 | 15 | 1500 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 200 | 300 | 0 | 1 | 4500 | 15 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
2 | LOAD 2 | COMBO STARTER | 1 | FUSE | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 500 | 600 | 0 |  | 9000 | 20 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
3 | LOAD 3 | COMBO STARTER | 1 | FUSE | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 800 | 900 | 0 |  |  | 25 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
4 | LOAD 4 | COMBO STARTER | 3Y | FUSE | 30 | 30 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 1000 | 1100 | 1200 | 1 |  | #14 | 30 |  | LOAD 4 |  | 30 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 1000 | 1100 | 1200 |  | MANUAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 14400 | 480 | 1.732 | 17.321 | 69.2841 | 4800 | 14400 | 480 | 1.732 | 17.321
5 | LOAD 5 | COMBO STARTER | 1 | FUSE | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 1400 | 1500 | 0 |  | #8 | 35 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
6 | LOAD 6 | COMBO STARTER | 1 | FUSE | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600 | 1700 | 1800 | 0 |  |  | 40 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
7 | LOAD 7 | COMBO STARTER | 1 | FUSE | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1900 | 2000 | 2100 | 0 |  |  | 45 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
8 | LOAD 8 | COMBO STARTER | 1 | FUSE | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2200 | 2300 | 2400 | 0 |  |  | 50 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
9 | LOAD 9 | COMBO STARTER | 1 | FUSE | 70 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2500 | 2600 | 2700 | 0 |  |  | 60 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
10 | LOAD 10 | COMBO STARTER | 1 | FUSE | 80 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 2900 | 3000 | 0 |  |  | 70 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
11 | LOAD 11 | COMBO STARTER | 1 | FUSE | 90 | 80 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3100 | 3200 | 3300 | 0 |  |  | 80 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
12 | LOAD 12 | COMBO STARTER | 1 | FUSE | 100 | 90 | 0 | 0 |  |  | ALL CELLS ARE PROTECTED IN DEMO VERSION |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3400 | 3500 | 3600 | 0 |  |  | 90 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
13 | LOAD 13 | COMBO STARTER | 1 | FUSE | 110 | 100 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3700 | 3800 | 3900 | 0 |  |  | 100 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
14 | LOAD 14 | COMBO STARTER | 1 | FUSE | 125 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 4100 | 4200 | 0 |  |  | 110 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
15 | LOAD 15 | COMBO STARTER | 1 | FUSE | 150 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4300 | 4400 | 4500 | 0 |  |  | 125 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
16 | LOAD 16 | COMBO STARTER | 1 | FUSE | 175 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4600 | 4700 | 4800 | 0 |  |  | 150 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
17 | LOAD 17 | COMBO STARTER | 1 | FUSE | 200 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4900 | 5000 | 5100 | 0 |  |  | 175 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
18 | LOAD 18 | COMBO STARTER | 1 | FUSE | 225 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5200 | 5300 | 5400 | 0 |  |  | 200 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 1 | 0 | 0 | 0 | 0 | 480 | 1 | 0
19 | LOAD 19 | COMBO STARTER | 1 | FUSE | 250 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5500 | 5600 | 5700 | 0 |  |  | 225 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | LOAD 20 | COMBO STARTER | 1 | FUSE | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5800 | 5900 | 6000 | 0 |  |  | 250 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | LOAD 21 | COMBO STARTER | 1 | FUSE | 350 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6100 | 6200 | 6300 | 0 |  |  | 300 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | LOAD 22 | COMBO STARTER | 1 | FUSE | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6400 | 6500 | 6600 | 0 |  |  | 350 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | LOAD 23 | COMBO STARTER | 1 | FUSE | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6700 | 6800 | 6900 | 0 |  |  | 400 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | LOAD 24 | COMBO STARTER | 1 | FUSE | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 7100 | 7200 | 0 |  |  | 450 | [31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500
[35 empty] | 600 |  | TOTALS |  | TOTALS | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 1000 | 1100 | 1200
700
[35 empty] | 800 | [6 empty] | 0 | [23 empty] | MLOAD | 0
[35 empty] | 1000 | [30 empty] | ERROR
[35 empty] | 1200 |  |  |  | 3Y | [26 empty] | CHECK
[35 empty] | 1600 |  |  |  |  | L2 |  |  | 1-POLE
[35 empty] | 2000 |  |  | SPACE | AMPS | AMPS | A SPACE
[35 empty] | 2500 | 1 | BREAKER |  |  | 15 | A | 2-POLE | (L1 & L2) | [7 empty] | SINGLE PHASE
[35 empty] | 3000 | 1 | FUSE |  |  | 20 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[35 empty] | 4000 | 1 | FUSE |  |  | 25 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[35 empty] | 5000 | 3Y | FUSE |  | 30 | 30 | A | FUSE | [5 empty] | 30A FUSE
[35 empty] | 6000 | 1 | FUSE |  |  | 35 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 40 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 45 | A | FUSE | (L1 & L2) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 50 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 60 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 70 | A | FUSE | (L1 & L2) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 80 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 90 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 100 | A | FUSE | (L1 & L2) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 110 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 125 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 150 | A | FUSE | (L1 & L2) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 175 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 200 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 250 | A | FUSE | (L1 & L2) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 300 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 350 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 400 | A | FUSE | (L1 & L2) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 450 | A | FUSE | (L2 &L3) | [7 empty] | SINGLE PHASE
[36 empty] | 1 | FUSE |  |  | 500 | A | FUSE | (L1 &L3) | [7 empty] | SINGLE PHASE

## M Feeders
3Y
Manual Feeder Imput | [47 empty] | 3Y |  |  | 3Y
[9 empty] | WIRE | WIRE | WIRE | WIRE
CIR | DESCRIPTION | NUMBER OF | LENGTH OF | CONDUIT | CONDUIT |  | WIRE | WIRE | SIZE | SIZE | SIZE | SIZE | [26 empty] | PHASE | SPACE | # | DASK | SIZE | SPACE | TYPE | SPACE | CU/AL |  |  | SPACE | # | DASK | SIZE | SPACE | TYPE | SPACE | CU/AL |  | SPACE | # | DASK | SIZE | SPACE | TYPE | SPACE | CU/AL |  |  |  | SPACE | # | DASK | SIZE | SPACE | CU/AL | SPACE
| OF LOAD | CONDUITS | CONDUIT | SIZE | TYPE |  | TYPE | CU or AL |  | (L2) | NEUTRAL | GROUND |  | 0 | [17 empty] | SPACE |  |  |  | SPACE
1 | LOAD 1 | 1 | 150 | 1 1/2" | RIGID |  | THW | CU | #14 | #14 | #10 | #6 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 150 | ' | 150' | 1/2" |  | 1 | - | 1 1/2" |  | RIGID | 1-1 1/2" RIGID | 1 |  | 2 | - | #14 |  | THW |  | CU | (L1 & L2) | 2-#14 THW CU (L1 & L2) |  | 1 | - | #14 |  | THW |  | CU | (L2) |  | 1 | - | #10 |  | THW |  | CU | (N) | 1-#10 THW CU (N) | 1 |  | 1 | - | #6 |  | CU | GND | 1-#6 CU GND | 0 | 1 | 1 | 1-#10 THW CU (N) | 1-#6 CU GND | 1-#10 THW CU (N) | 1-#6 CU GND
2 | LOAD 2 | 1 | 60 | 1 1/2" | RIGID |  | THHN | CU | #8 | #12 | #1 | #6 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | ' | 60' | 3/4" |  | 1 | - | 1 1/2" |  | RIGID | 1-1 1/2" RIGID | 1 |  | 2 | - | #8 |  | THHN |  | CU | (L1 & L2) | 2-#8 THHN CU (L1 & L2) |  | 1 | - | #12 |  | THHN |  | CU | (L2) |  | 1 | - | #1 |  | THHN |  | CU | (N) | 1-#1 THHN CU (N) | 1 |  | 1 | - | #6 |  | CU | GND | 1-#6 CU GND | 0 | 1 | 1 | 1-#1 THHN CU (N) | 1-#6 CU GND | 1-#1 THHN CU (N) | 1-#6 CU GND
3 | LOAD 3 | 1 | 30 | 1" | RIGID |  | THW | CU | #8 | #8 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NONE | 0 | 30 | ' | 30' | 1" |  | 1 | - | 1" |  | RIGID | 1-1" RIGID | 1 |  | 2 | - | #8 |  | THW |  | CU | (L1 & L2) | 2-#8 THW CU (L1 & L2) |  | 1 | - | #8 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
4 | LOAD 4 | 1 | 80 | 3/4" | EMT |  | THHN | CU | #10 | #4 | NONE | #12 | 3Y | 1 | MANUAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #14 | 0 | 80 | ' | 80' | 1 1/4" |  | 1 | - | 3/4" |  | EMT | 1-3/4" EMT | 3Y |  | 3 | - | #10 |  | THHN |  | CU |  | 3-#10 THHN CU |  | 1 | - | #4 |  | THHN |  | CU | (L2) |  | 1 | - | NONE |  | THHN |  | CU | (N) |  | 3Y |  | 1 | - | #12 |  | CU | GND | 1-#12 CU GND | 0 | 0 | 1 |  | 1-#12 CU GND | 1-#12 CU GND
5 | LOAD 5 | 1 | 50 | 1" | EMT |  | THHN | CU | #6 | #10 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #12 | 0 | 50 | ' | 50' | 1 1/2" |  | 1 | - | 1" |  | EMT | 1-1" EMT | 1 |  | 2 | - | #6 |  | THHN |  | CU | (L1 & L2) | 2-#6 THHN CU (L1 & L2) |  | 1 | - | #10 |  | THHN |  | CU | (L2) |  | 1 | - | #14 |  | THHN |  | CU | (N) | 1-#14 THHN CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THHN CU (N) | 1-#14 CU GND | 1-#14 THHN CU (N) | 1-#14 CU GND
6 | LOAD 6 | 1 | 60 | 1/2" | RIGID |  | THW | CU | #3 | #4 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #10 | 0 | 60 | ' | 60' | 2" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #3 |  | THW |  | CU | (L1 & L2) | 2-#3 THW CU (L1 & L2) |  | 1 | - | #4 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
7 | LOAD 7 | 1 | 70 | 1/2" | RIGID |  | THW | CU | #2 | #3 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #8 | 0 | 70 | ' | 70' | 2 1/2" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #2 |  | THW |  | CU | (L1 & L2) | 2-#2 THW CU (L1 & L2) |  | 1 | - | #3 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
8 | LOAD 8 | 1 | 80 | 1/2" | RIGID |  | THW | CU | #1 | #2 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #6 | 0 | 80 | ' | 80' | 3" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #1 |  | THW |  | CU | (L1 & L2) | 2-#1 THW CU (L1 & L2) |  | 1 | - | #2 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
9 | LOAD 9 | 1 | 90 | 1/2" | RIGID |  | THW | CU | #1/0 | #1 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #4 | 0 | 90 | ' | 90' | 3 1/2" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #1/0 |  | THW |  | CU | (L1 & L2) | 2-#1/0 THW CU (L1 & L2) |  | 1 | - | #1 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
10 | LOAD 10 | 1 | 100 | 1/2" | RIGID |  | THW | CU | #2/0 | #1/0 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #3 | 0 | 100 | ' | 100' | 4" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #2/0 |  | THW |  | CU | (L1 & L2) | 2-#2/0 THW CU (L1 & L2) |  | 1 | - | #1/0 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
11 | LOAD 11 | 1 | 110 | 1/2" | RIGID |  | THW | CU | #3/0 | #2/0 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #2 | 0 | 110 | ' | 110' | 5" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #3/0 |  | THW |  | CU | (L1 & L2) | 2-#3/0 THW CU (L1 & L2) |  | 1 | - | #2/0 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
12 | LOAD 12 | 1 | 120 | [5 empty] | #4/0 | #3/0 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #1 | 0 | 120 | ' | 120' | 6" |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #4/0 |  | THW |  | CU | (L1 & L2) | 2-#4/0 THW CU (L1 & L2) |  | 1 | - | #3/0 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
13 | LOAD 13 | 1 | 130 |  |  | ALL CELLS ARE PROTECTED IN DEMO VERSION |  |  | #250 | #4/0 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #1/0 | 0 | 130 | ' | 130' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #250 |  | THW |  | CU | (L1 & L2) | 2-#250 THW CU (L1 & L2) |  | 1 | - | #4/0 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
14 | LOAD 14 | 1 | 140 | [5 empty] | #300 | #250 | #14 | #14 | 1 | 0 | XMFR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #2/0 | 0 | 140 | ' | 140' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #300 |  | THW |  | CU | (L1 & L2) | 2-#300 THW CU (L1 & L2) |  | 1 | - | #250 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
15 | LOAD 15 | 1 | 150 | 1/2" | RIGID |  | THW | CU | #350 | #300 | #14 | #14 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #3/0 | 0 | 150 | ' | 150' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #350 |  | THW |  | CU | (L1 & L2) | 2-#350 THW CU (L1 & L2) |  | 1 | - | #300 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
16 | LOAD 16 | 1 | 160 | 1/2" | RIGID |  | THW | CU | #400 | #350 | #14 | #14 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #4/0 | 0 | 160 | ' | 160' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #400 |  | THW |  | CU | (L1 & L2) | 2-#400 THW CU (L1 & L2) |  | 1 | - | #350 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
17 | LOAD 17 | 1 | 170 | 1/2" | RIGID |  | THW | CU | #500 | #400 | #14 | #14 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #250 | 0 | 170 | ' | 170' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #500 |  | THW |  | CU | (L1 & L2) | 2-#500 THW CU (L1 & L2) |  | 1 | - | #400 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
18 | LOAD 18 | 1 | 180 | 1/2" | RIGID |  | THW | CU | #600 | #500 | #14 | #14 | 1 | 0 | MANUAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #300 | 0 | 180 | ' | 180' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #600 |  | THW |  | CU | (L1 & L2) | 2-#600 THW CU (L1 & L2) |  | 1 | - | #500 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
19 | LOAD 19 | 1 | 190 | 1/2" | RIGID |  | THW | CU | #250 | #4/0 | #14 | #14 | 1 | 0 | MANUAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #350 | 0 | 190 | ' | 190' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #250 |  | THW |  | CU | (L1 & L2) | 2-#250 THW CU (L1 & L2) |  | 1 | - | #4/0 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
20 | LOAD 20 | 1 | 200 | 1/2" | RIGID |  | THW | CU | #300 | #250 | #14 | #14 | 1 | 0 | SPACE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #400 | 0 | 200 | ' | 200' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #300 |  | THW |  | CU | (L1 & L2) | 2-#300 THW CU (L1 & L2) |  | 1 | - | #250 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
21 | LOAD 21 | 1 | 210 | 1/2" | RIGID |  | THW | CU | #350 | #300 | #14 | #14 | 1 | 0 | SPACE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #500 | 0 | 210 | ' | 210' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #350 |  | THW |  | CU | (L1 & L2) | 2-#350 THW CU (L1 & L2) |  | 1 | - | #300 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
22 | LOAD 22 | 1 | 220 | 1/2" | RIGID |  | THW | CU | #400 | #350 | #14 | #14 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #600 | 0 | 220 | ' | 220' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #400 |  | THW |  | CU | (L1 & L2) | 2-#400 THW CU (L1 & L2) |  | 1 | - | #350 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
23 | LOAD 23 | 1 | 230 | 1/2" | RIGID |  | THW | CU | #500 | #400 | #14 | #14 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #750 | 0 | 230 | ' | 230' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #500 |  | THW |  | CU | (L1 & L2) | 2-#500 THW CU (L1 & L2) |  | 1 | - | #400 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
24 | LOAD 24 | 1 | 240 | 1/2" | RIGID |  | THW | CU | #600 | #500 | #14 | #14 | 1 | 0 | PANEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #1000 | 0 | 240 | ' | 240' |  |  | 1 | - | 1/2" |  | RIGID | 1-1/2" RIGID | 1 |  | 2 | - | #600 |  | THW |  | CU | (L1 & L2) | 2-#600 THW CU (L1 & L2) |  | 1 | - | #500 |  | THW |  | CU | (L2) |  | 1 | - | #14 |  | THW |  | CU | (N) | 1-#14 THW CU (N) | 1 |  | 1 | - | #14 |  | CU | GND | 1-#14 CU GND | 0 | 1 | 1 | 1-#14 THW CU (N) | 1-#14 CU GND | 1-#14 THW CU (N) | 1-#14 CU GND
[15 empty] | FEEDER | 0
ERROR

## Calcs
[13 empty] | LOAD CALCULATIONS FOR - |  |  | CODE YEAR | 2008
LOAD CALCULATIONS FOR - MAIN SWITCHBOARD | [12 empty] | MAIN SWITCHBOARD |  |  | BASED ON THE 2008 NEC | [11 empty] | ERRORS
BASED ON THE 2008 NEC | [9 empty] | NEC 220.61(A) | [14 empty] | INPUT | 0 | MLOADS | 0 | ERROR ON M-LOADS TAB
|  |  | L1 |  | L2 |  | L3 |  |  | NEUTRAL |  |  | LOAD CALCULATIONS FOR - MAIN SWITCHBOARD | [11 empty] | PANEL | 0 | MFEEDERS | 0 | ERROR ON M-FEEDERS TAB
CALCULATED LOAD ( NEC 215.5 ) |  |  | 89740 | VA | 85340 | VA | 79240 | VA | 89740 | VA | 254320 |  | MASTER ERROR | 0 | [10 empty] | MLOADS | 0 | PANEL | 0 | ERROR IN PANEL TEMPLATE |  | 0 | ERROR IN PANEL TEMPLATE
[25 empty] | MFEEDERS | 0 | INPUT | 0 | ERROR ON INPUT TAB
CALCULATED LOAD WITH DEMAND FACTORS ( NEC 215.5 ) | [12 empty] | PHASE | 3Y | [12 empty] | UPDATE | 0 | PANEL TEMPLATES NEED UPDATING OR HAVE ERRORS
| GENERAL LOAD |  | 22000 | VA | 22000 | VA | 14200 | VA | 22000 | VA |  |  | HI VOTLS | 480
| RECEPTACLE LOAD (NEC TABLE 220.44) | [11 empty] | LOW VOTLS | 277
|  | 1ST 10,000W | 3553.5007 | VA | 3223.2497 | VA | 3223.2497 | VA | 3553.5007 | VA | [16 empty] | GRAND | 0
|  | REMAINDER @ 50% | 6293 | VA | 5708 | VA | 5708 | VA | 6293 | VA |  |  | NEUTRAL SIZE | AUTO | [12 empty] | ERROR
| CONTINUOUS LOAD (NEC 215.2) |  | 30000 | VA | 28000 | VA | 28500 | VA | 30000 | VA |  |  | HI-LEG SIZE | AUTO
|  | PLUS 25% (L1, L2, L3) | 7500 | VA | 7000 | VA | 7125 | VA |  |  |  |  | FACTOR | 0
|  | PLUS 0% (NEUTRAL) NEC 215.2(A) EX NO 2 | [6 empty] | 0 | VA |  |  | FACTOR L2 | 20
| MOTOR LOAD (NEC 430.24) |  | 14700 | VA | 14700 | VA | 14700 | VA | 14700 | VA |  |  | TRANS 0 OR 1 |  |  | 44100 | 53
|  | PLUS 25% OF LARGEST MOTOR | 1250 | VA | 1250 | VA | 1250 | VA | 1250 | VA |  |  | PHASE SOURCE |  |  | 212
| KITCHEN LOADS (NEC 220.56) | [11 empty] | SERVICE SIZING | AUTO
|  | L1 ( 6,900 X 0.65 ) = | 4485 | VA |  |  |  |  | 4485 | VA
|  | L2 ( 6,000 X 0.65 ) = |  |  | 3900 | VA
|  | L3 ( 7,200 X 0.65 ) = |  |  |  |  | 4680 | VA |  |  | 254949 |  |  | L1 | 89782 | 10396 | 4001 | 4001
TOTAL BALANCED LOAD (3-PHASE) |  |  | 79386 | VA | 79386 | VA | 79386 | VA | [5 empty] | L2 | 85781 | 6395 | 0 | 0
TOTAL BALANCED LOAD (1-PHASE) |  |  | 6395 | VA | 6395 | VA | 0 | VA | [5 empty] | L3 | 79386
TOTAL UNBALANCED LOAD (1-PHASE) |  |  | 4001 | VA | 0 | VA | 0 | VA | [5 empty] | 254949 | 254949 | 6395
[9 empty] | 82281.5007 | VA | 254949 |  |  | 3-PHASE DELTA |  | 2 | 4001
LOAD ERROR
LINE AMPS BALANCED (3-PHASE) |  |  | 286.5 | A | 286.5 | A | 286.5 | A | [5 empty] | 0
LINE AMPS BALANCED (1-PHASE) |  |  | 26.6458 | A | 26.6458 | A | 0 | A
LINE AMPS UNBALANCED (1-PHASE) |  |  | 14.444 | A | 0 | A | 0 | A | [5 empty] | BUS AMPS | 3000 |  |  | DESIGN LOAD IS |  | 327.6 | A | DESIGN LOAD IS 327.6A
| TOTALS |  | 327.5899 | A | 313.1458 | A | 286.5 | A | 297 | A |  |  |  | MAX LOAD | 327.6
| ADJUSTMENT FACTOR |  | 0 | A | 0 | A | 0 | A | 0 | A |  |  |  | MIN AMPS | 0 |  | 350
TOTAL DESIGN LOAD |  |  | 327.6 | A | 313.1 | A | 286.5 | A | 297 | A |  |  |  | MAX | 327.6 |  | 350 | A | - | 480 | / | 277 | V - | THREE PHASE WYE | 350 A - 480 / 277 V - THREE PHASE WYE
3000
HARMONIC CURRENT CALCULATION ( NEC 310.15 (B) 4 (C) & NEC TABLE 310.15 B (2) A ) | [13 empty] | AUTO
| ( Harmonic Load 0 VA ÷ Connected Load 202,120 VA ) X 100 = 0 % | [12 empty] | CONDUIT
| Harmonic Load Does Not Exceed 50% | [18 empty] | NEUTRAL AMPS 2008 NEC
82282
FAULT CURRENT CALCULATIONS | [13 empty] | FAULT METHOD | 5 |  |  |  |  | L1 | 82282 | 1
|  | Available Fault Current at Starting Point (( 44,903 AFC x 1.00 UA ) + 212 MC ) = 45,115 AFC | [17 empty] | L2 | 78781 | 0
|  | Conductor Factor CF - Formula ( 1.732 x 100 L x 45,115 AFC ) ÷ ( 20,566 C x 1 N x 480 SV ) = 0.792 CF | [8 empty] | Conductor Factor CF - Formula ( 1.732 x 100 L x 45,115 AFC ) ÷ ( 20,566 C x 1 N x 480 SV ) = 0.792 CF | [8 empty] | L3 | 72261 | 0
|  | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 0.792 CF ) = 0.558 CM | [11 empty] | AUTO |  | MAN FUSE SIZE |  | 4000
|  | Conductor Let-Through Current CLC - Formula ( 45,115 AFC x 0.558 CM ) = 25,174 CLC | [13 empty] | AUTO FUSE SIZE |  | 350 |  | MAX VA | 82282 | 1
[13 empty] | AFC K | 25.2 K |  | 25.2 K | 45.1 K | 1 |  | VA X 3 | 246846
[6 empty] | ALL CELLS ARE PROTECTED IN DEMO VERSION | [6 empty] | AFC | 25174 |  | 25174 | 45115 | 0 |  | AMPS | 296.9
[13 empty] | AF | 25174
[16 empty] | 44903 |  | EMPTY CONDUIT
A - Amps |  |  | N - Number of Conductors Per Phase | [12 empty] | 44.9 | K | 44.9 K
AFC - Available Fault Current |  |  | SV - Secondary Voltage
C - Conductor Constant |  |  | UA - Utility Adjustment
CF - Conductor Factor |  |  | VA - Volt Amps
CLC - Conductor Let-Through Current
CM - Conductor Multiplier | [12 empty] | HARMONIC LOAD | 0
L - Length of Conductor | [12 empty] | TOTAL LOAD | 202120
MC - Motor Contribution | [12 empty] | HARMONIC % | 0
| Prepared With 1-Line 2011 Software - Copyright Durand & Associates | [12 empty] | ( | Harmonic Load | 0 | VA ÷ | Connected Load | 202,120 | VA ) X 100 = | 0 | % | ( Harmonic Load 0 VA ÷ Connected Load 202,120 VA ) X 100 = 0 %
[13 empty] | NEUTRAL AMPS | AUTO
[13 empty] | NEUTRAL LOAD | 0
[13 empty] | 1-PHASE | 0
[13 empty] | AMPS | 0
[13 empty] | 3-PHASE DELTA | 40
[13 empty] | AMPS | 0.1444
[13 empty] | 3-PHASE Y | 0
[13 empty] | AMPS | #VALUE!
[13 empty] | MAX LINE AMPS | 0
[20 empty] | ( | 30 | ' X
[12 empty] | AUTO |  |  |  |  | NONE |  |  |  |  | AUTO |  |  | AUTO |  |  |  |  | AUTO
[17 empty] | 5 |  |  |  |  | 1&2 |  |  | 3&4 |  |  |  |  | 5&6
[12 empty] | A - Amps |  |  |  |  | A - Amps |  |  |  |  | %Z - Transformer Impedance Nameplate %Z |  |  | %Z - Transformer Impedance Nameplate %Z |  |  |  |  | A - Amps
[12 empty] | AFC - Available Fault Current |  |  |  |  | AFC - Available Fault Current |  |  |  |  | A - Amps |  |  | A - Amps |  |  |  |  | AFC - Available Fault Current
[12 empty] | C - Conductor Constant |  |  |  |  | C - Conductor Constant |  |  |  |  | AFC - Available Fault Current |  |  | AFC - Available Fault Current |  |  |  |  | C - Conductor Constant
[12 empty] | CF - Conductor Factor |  |  |  |  | CF - Conductor Factor |  |  |  |  | C - Conductor Constant |  |  | C - Conductor Constant |  |  |  |  | CF - Conductor Factor
[12 empty] | CLC - Conductor Let-Through Current |  |  |  |  | CLC - Conductor Let-Through Current |  |  |  |  | CF - Conductor Factor |  |  | CF - Conductor Factor |  |  |  |  | CLC - Conductor Let-Through Current
[12 empty] | CM - Conductor Multiplier |  |  |  |  | CM - Conductor Multiplier |  |  |  |  | CLC - Conductor Let-Through Current |  |  | CLC - Conductor Let-Through Current |  |  |  |  | CM - Conductor Multiplier
[12 empty] | L - Length of Conductor |  |  |  |  | L - Length of Conductor |  |  |  |  | CM - Conductor Multiplier |  |  | CM - Conductor Multiplier |  |  |  |  | L - Length of Conductor
[12 empty] | MC - Motor Contribution |  |  |  |  | MC - Motor Contribution |  |  |  |  | FLA - Full Load Amps |  |  | KVA - Kilovolt Amps |  |  |  |  | MC - Motor Contribution
[12 empty] | N - Number of Conductors Per Phase |  |  |  |  | N - Number of Conductors Per Phase |  |  |  |  | KVA - Kilovolt Amps |  |  | L - Length of Conductor |  |  |  |  | N - Number of Conductors Per Phase
[12 empty] | SV - Secondary Voltage |  |  |  |  | SV - Secondary Voltage |  |  |  |  | L - Length of Conductor |  |  | MC - Motor Contribution |  |  |  |  | SV - Secondary Voltage
[12 empty] | UA - Utility Adjustment |  |  |  |  | UA - Utility Adjustment |  |  |  |  | MC - Motor Contribution |  |  | N - Number of Conductors Per Phase |  |  |  |  | UA - Utility Adjustment
[12 empty] | VA - Volt Amps |  |  |  |  | VA - Volt Amps |  |  |  |  | N - Number of Conductors Per Phase |  |  | PV - Primary Voltage |  |  |  |  | VA - Volt Amps
[22 empty] | SV - Secondary Voltage |  |  | SV - Secondary Voltage
[22 empty] | TLC - Transformer Let-Through Current |  |  | TF - Transformer Factor
[22 empty] | TM - Transformer Multiplier |  |  | TLC - Transformer Let-Through Current
[22 empty] | UA - Utility Adjustment |  |  | TM - Transformer Multiplier
[22 empty] | VA - Volt Amps |  |  | UA - Utility Adjustment
VA - Volt Amps
[22 empty] | NONE |  |  | NONE |  |  |  |  | NONE
[22 empty] | 1&2 |  |  | 3&4 |  |  |  |  | 5&6
[17 empty] | A - Amps |  |  |  |  | %Z - Transformer Impedance Nameplate %Z |  |  | %Z - Transformer Impedance Nameplate %Z |  |  |  |  | A - Amps
[12 empty] | A - Amps |  |  |  |  | AFC - Available Fault Current |  |  |  |  | A - Amps |  |  | A - Amps |  |  |  |  | AFC - Available Fault Current
[12 empty] | AFC - Available Fault Current |  |  |  |  | MC - Motor Contribution |  |  |  |  | AFC - Available Fault Current |  |  | AFC - Available Fault Current |  |  |  |  | MC - Motor Contribution
[12 empty] | MC - Motor Contribution |  |  |  |  | UA - Utility Adjustment |  |  |  |  | FLA - Full Load Amps |  |  | KVA - Kilovolt Amps |  |  |  |  | UA - Utility Adjustment
[12 empty] | UA - Utility Adjustment 1.1 |  |  |  |  | VA - Volt Amps |  |  |  |  | KVA - Kilovolt Amps |  |  | MC - Motor Contribution |  |  |  |  | VA - Volt Amps
[12 empty] | VA - Volt Amps | [9 empty] | MC - Motor Contribution |  |  | PV - Primary Voltage
[22 empty] | SV - Secondary Voltage |  |  | SV - Secondary Voltage
[22 empty] | TLC - Transformer Let-Through Current |  |  | TF - Transformer Factor
[22 empty] | TM - Transformer Multiplier |  |  | TLC - Transformer Let-Through Current
[22 empty] | UA - Utility Adjustment |  |  | TM - Transformer Multiplier
[22 empty] | VA - Volt Amps |  |  | UA - Utility Adjustment
VA - Volt Amps

## 1-Line
ERROR | 0
CIRCUITS | 4
CT | YES
METER | YES |  |  |  |  | 25.2 K | CT |  |  | 350A |  | 350 A - 480 / 277 V - THREE PHASE WYE
MAIN | YES | 350A | [7 empty] | MAIN BKR
SHOW_VD | YES
SHOW_AFC | YES | [5 empty] | METER
SHOW_LENGTH | YES
UNDER_OVER | OVER | [11 empty] | ( | 150A 3-POLE | ( | 125A 3-POLE |  | ( | 90A 3-POLE |  | ( | 30A FUSE
SHOW_FILE | YES
FEEDER_SIZING | AUTO | [11 empty] | 25.2 K |  | 25.2 K |  |  | 25.2 K |  |  | 25.2 K
GROUND | YES |  |  |  |  | 100' | [7 empty] | 15' |  | 15' |  |  | 15' |  |  | 80' | [14 empty] | 180' |  | 190'
GENSET | GENSET |  |  |  |  | 1-3'' RIGID | [7 empty] | 1-1 1/2'' EMT |  | 1-1 1/2'' EMT |  |  | 1-1'' EMT |  |  | 1-3/4" EMT | [14 empty] | 1-1/2" RIGID |  | 1-1/2" RIGID
ATS | ATS |  |  |  |  | 4-#400 THHN CU |  |  |  |  | #4 CU |  |  | 4-#1/0 THHN CU |  | 4-#1 THHN CU |  |  | 3-#4 THHN CU |  |  | 3-#10 THHN CU | [14 empty] | 2-#600 THW CU (L1 & L2) |  | 2-#250 THW CU (L1 & L2)
CIR_01 | PP |  | / | \ | [6 empty] | TO UFER GND |  |  | 1-#6 CU GND |  | 1-#6 CU GND |  |  | 1-#8 CU GND |  |  | 1-#12 CU GND | [14 empty] | 1-#14 THW CU (N) |  | 1-#14 THW CU (N)
CIR_02 | PTP | 0 | 45.1 K | [7 empty] | NEC 250.66(B) | [25 empty] | 1-#14 CU GND |  | 1-#14 CU GND
CIR_03 | XP | 0
CIR_04 | MC | 0
CIR_05 | XP | 0 | [10 empty] | 21.9 K | 0.1 % VD | 21.2 K | 0.1 % VD |  | 18.5 K | 0.1 % VD |  | 2.6 K | 0.6 % VD | [13 empty] | #VALUE! | 0 % VD | #VALUE! | 0 % VD
CIR_06 | XP | 0 |  |  | \ | / | [11 empty] | \/\/\/\/\/\/\/ |  |  | DISC |  | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ |  |  |  | DISC |  | DISC
CIR_07 | XP | 0 | [10 empty] | ATS |  | PANEL |  |  | 60 KVA |  |  | M/STR | [11 empty] | PANEL | PANEL | PANEL | M/STR |  | M/STR |  | PANEL | PANEL | PANEL
CIR_09 | XP | 0 | [10 empty] | 200A |  | P |  |  | /\/\/\/\/\/\/\ |  | --- #4 GND | LOAD 4 |  | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\
CIR_09 | XP | 0 | [15 empty] | 5.8 K
CIR_10 | XP | 0
CIR_11 | XP | 0 | [5 empty] | 25' | [5 empty] | 15' |  | 20' |  |  | 20'
CIR_12 | XP | 0 | [5 empty] | 1-1 1/2'' EMT | [5 empty] | 1-1 1/2'' EMT |  | 1-3/4'' EMT |  |  | 1-2'' EMT |  |  | 1-3/4" EMT | [14 empty] | 1-1/2" RIGID |  | 1-1/2" RIGID
CIR_13 | XP | 0 | [5 empty] | 4-#1/0 THHN CU | [5 empty] | 4-#1/0 THHN CU |  | 3-#6 THHN CU |  |  | 4-#2/0 THHN CU |  |  | 3-#10 THHN CU | [14 empty] | 2-#600 THW CU (L1 & L2) |  | 2-#250 THW CU (L1 & L2)
CIR_14 | XP | 0 | [5 empty] | 1-#6 CU GND | [5 empty] | 1-#6 CU GND |  | 1-#8 CU GND |  |  | 1-#1 THHN CU (N) |  |  | 1-#12 CU GND | [14 empty] | 1-#14 THW CU (N) |  | 1-#14 THW CU (N)
CIR_15 | PTP | 0 | [16 empty] | 1-#6 CU GND | [17 empty] | 1-#14 CU GND |  | 1-#14 CU GND
CIR_16 | PTP | 0
CIR_17 | PTP | 0
CIR_18 | MC | 0 | [10 empty] | 19.4 K | 0.1 % VD | 13 K | 0.2 % VD |  | 5.3 K | 0.2% VD
CIR_19 | MC | 0 | [12 empty] | \/\/\/\/\/\/\/ | [5 empty] | MOTOR | [11 empty] | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | MOTOR |  | MOTOR |  | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/ | \/\/\/\/\/\/\/
CIR_20 | S | 0 |  | GENERATOR |  |  | ( | 150A 3-POLE |  |  |  |  | PANEL |  | 45 KVA |  |  | PANEL |  |  |  |  | PANEL | PANEL | PANEL | PANEL | PANEL | PANEL | PANEL | PANEL | PANEL | PANEL
CIR_21 | S | 0 |  | 150 KW | [8 empty] | P |  | /\/\/\/\/\/\/\ |  | --- #6 GND | XP | [14 empty] | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ |  |  |  |  | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\ | /\/\/\/\/\/\/\
CIR_22 | PTP | 0 |  | 480/277V - 3-PHASE WYE | [10 empty] | 4.4 K
CIR_23 | PTP | 0
CIR_24 | PTP | 0 | [11 empty] | 30' |  | 30'
[14 empty] | 1-1 1/4'' EMT |  | 1-1 1/2'' EMT
METER_01 | NO | [7 empty] | 1-#6 GND |  |  |  |  | 4-#4 THHN CU |  | 4-#1 THHN CU
METER_02 | NO | [12 empty] | 1-#6 THHN CU (N) |  | 1-#2 THHN CU (N)
METER_03 | NO | [12 empty] | 1-#8 CU GND |  | 1-#6 CU GND
METER_04 | NO | [19 empty] | ALL CELLS ARE PROTECTED IN DEMO VERSION
METER_05 | NO
METER_06 | NO | [11 empty] | 12.5 K | 0.2% VD | 3.8 K | 0.4% VD
METER_07 | NO
METER_09 | NO | [11 empty] | PANEL |  | PANEL | [17 empty] | PANEL | PANEL | PANEL |  |  |  |  | PANEL | PANEL | PANEL
METER_09 | NO | [11 empty] | SP |  | SP2
METER_10 | NO
METER_11 | NO
METER_12 | NO
METER_13 | NO
METER_14 | NO
METER_15 | NO
METER_16 | NO
METER_17 | NO
METER_18 | NO
METER_19 | NO
METER_20 | NO
METER_21 | NO
METER_22 | NO
METER_23 | NO
METER_24 | NO
VD AT ATS | 0.1 % VD

## Load Summary
ERROR | 0 | [14 empty] | AUTO | [14 empty] | 3Y
UPDATE | 0 | LOAD SUMMARY - MSWBD | [13 empty] | 2008 | LOAD SUMMARY - MSWBD | [13 empty] | 1
| 0 | [14 empty] | ATS
PHASE | 0 | CIRCUIT | LOAD | CALCULATED LOAD |  |  | GENERAL LOAD |  |  | RECEPTACLE |  |  | CONTINUOUS LOAD |  |  | GENSET | CIRCUIT | LOAD | CALCULATED LOAD |  |  | GENERAL LOAD |  |  | RECEPTACLE |  |  | CONTINUOUS LOAD |  |  |  | CIRCUIT | LOAD | CALCULATED LOAD ( NEC 215.5 ) |  |  | GENERAL LOAD |  |  | RECEPTACLE |  |  | CONTINUOUS LOAD |  |  | MOTOR LOAD |  |  | LARGEST MOTOR LOAD |  |  | KITCHEN LOAD |  |  | # OF | HARMONIC
4 |  |  |  | VA |  |  | VA |  |  | VA |  |  | VA |  |  | MANUAL | [38 empty] | KITCHEN | LOADS
|  |  |  | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 |  |  |  | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 |  |  |  | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | LOADS | L1 L2 L3
PANEL |  | 1 | P | 34200 | 33000 | 28700 | 7000 | 7000 | 4000 |  |  |  | 18000 | 18000 | 15500 |  | 1 | P | 34200 | 33000 | 28700 | 7000 | 7000 | 4000 |  |  |  | 18000 | 18000 | 15500 |  | 1 | P | 34200 | 33000 | 28700 | 7000 | 7000 | 4000 | 0 | 0 | 0 | 18000 | 18000 | 15500 | 6500 | 6500 | 6500 | 5000 | 5000 | 5000 | 2700 | 1500 | 2700 | 5 | 0
PANEL |  | 2 | P | 32740 | 29540 | 29540 | 6000 | 6000 | 3000 | 8640 | 8640 | 8640 | 10500 | 7000 | 10000 |  | 2 | P | 32740 | 29540 | 29540 | 6000 | 6000 | 3000 | 8640 | 8640 | 8640 | 10500 | 7000 | 10000 |  | 2 | P | 32740 | 29540 | 29540 | 6000 | 6000 | 3000 | 8640 | 8640 | 8640 | 10500 | 7000 | 10000 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 4200 | 4500 | 4500 | 3 | 0
XMFR |  | 3 | XP | 18000 | 18000 | 16200 | 9000 | 9000 | 7200 | 7500 | 6000 | 6000 | 1500 | 3000 | 3000 |  | 3 | XP | 18000 | 18000 | 16200 | 9000 | 9000 | 7200 | 7500 | 6000 | 6000 | 1500 | 3000 | 3000 |  | 3 | XP | 18000 | 18000 | 16200 | 9000 | 9000 | 7200 | 7500 | 6000 | 6000 | 1500 | 3000 | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MANUAL |  | 4 | LOAD 4 | 4800 | 4800 | 4800 | [10 empty] | 4 | LOAD 4 | 4800 | 4800 | 4800 | [10 empty] | 4 | LOAD 4 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | 0 | 0 | 0 | 0
ALL CELLS ARE PROTECTED IN DEMO VERSION
|  | TOTALS |  | 89740 | 85340 | 79240 | 22000 | 22000 | 14200 | 16140 | 14640 | 14640 | 30000 | 28000 | 28500 |  | TOTALS |  | 89740 | 85340 | 79240 | 22000 | 22000 | 14200 | 16140 | 14640 | 14640 | 30000 | 28000 | 28500 |  | TOTALS |  | 89740 | 85340 | 79240 | 22000 | 22000 | 14200 | 16140 | 14640 | 14640 | 30000 | 28000 | 28500 | 14700 | 14700 | 14700 | 5000 | 5000 | 5000 | 6900 | 6000 | 7200 | 8 | 0
0
[49 empty] | 1250 | 1250 | 1250 | 4485 | 3900 | 4680
PHASE | 3Y | CIRCUIT | LOAD | MOTOR LOAD |  |  | LARGEST MOTOR LOAD |  |  | KITCHEN LOAD |  |  | # OF | HARMONIC |  |  | CIRCUIT | LOAD | MOTOR LOAD |  |  | LARGEST MOTOR LOAD |  |  | KITCHEN LOAD |  |  | # OF | HARMONIC | [6 empty] | 254320
|  |  |  | VA |  |  | VA |  |  | VA |  |  | KITCHEN | LOAD | [13 empty] | KITCHEN | LOAD | [6 empty] | 1831800
|  |  |  | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | LOADS | VA |  |  |  |  | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | LOADS
|  | 1 | P | 6500 | 6500 | 6500 | 5000 | 5000 | 5000 | 2700 | 1500 | 2700 | 5 |  |  | 1 | 1 | P | 6500 | 6500 | 6500 | 5000 | 5000 | 5000 | 2700 | 1500 | 2700 | 5 | [23 empty] | KITCHEN | 1 | 1
|  | 2 | P | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 4200 | 4500 | 4500 | 3 |  |  | 2 | 1 | LOAD 1 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 4200 | 4500 | 4500 | 3 | [23 empty] | LOADS | 2 | 1
|  | 3 | XP | [12 empty] | 3 | 1 | LOAD 1 | [34 empty] | 3 | 0.9
|  | 4 | LOAD 4 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | [6 empty] | 4 | 1 | LOAD 1 | 4800 | 4800 | 4800 | 4800 | 4800 | 4800 | [28 empty] | 4 | 0.8
[16 empty] | 5 | 1 | LOAD 1 | [34 empty] | 5 | 0.7
[16 empty] | 6 | 1 | LOAD 1 | [34 empty] | 6 | 0.65
[16 empty] | 7 | 1 | LOAD 1 | [33 empty] | 0.65
[16 empty] | 8 | 1 | LOAD 1
[16 empty] | 9 | 1 | LOAD 1
[16 empty] | 10 | 1 | LOAD 1
[16 empty] | 11 | 1 | LOAD 1
[16 empty] | 12 | 1 | LOAD 1
[16 empty] | 13 | 1 | LOAD 1
[16 empty] | 14 | 1 | LOAD 1
[16 empty] | 15 | 1 | LOAD 1
[16 empty] | 16 | 1 | LOAD 1
[16 empty] | 17 | 1 | LOAD 1
[16 empty] | 18 | 1 | LOAD 1
19
20
21
22
23
24
|  | TOTALS |  | 14700 | 14700 | 14700 | 5000 | 5000 | 5000 | 6900 | 6000 | 7200 | 8 |  |  |  | TOTALS |  | 14700 | 14700 | 14700 | 5000 | 5000 | 5000 | 6900 | 6000 | 7200 | 8
|  | CIRCUIT | LOAD | NEUTRAL LOAD |  |  |  | GENERATOR LOAD CALCULATION | [8 empty] | NEUTRAL LOAD
|  |  |  | VA | [12 empty] | VA
|  |  |  | L1 | L2 | L3 | [10 empty] | L1 | L2 | L3
|  | 1 | P |  |  |  |  | P |  | 110455 | VA
|  | 2 | P |  |  |  |  | MOTOR STARTING |  | 39000 | VA
|  | 3 | XP |  |  |  |  | TOTAL |  | 149455 | VA
|  | 4 | LOAD 4 |  |  |  |  | GENERATOR SIZE |  | 149 | KW
TOTALS
|  | MINIMUM NEUTRAL VA PER NEC 220.61(A) |  |  |  | 0

## Short 1 (hidden)
| AUTO | MAIN TRANSFORMER
UTILITY TRANSFORMER INFINITE BUS
|  | Step 1 - Transformer FLA | [6 empty] | 3Y |  |  |  |  | AFC - Assumes Unlimited Primary Short-Circuit Current ( Infinite Bus )
|  | Three Phase | [11 empty] | ÷
| Transformer FLA - Formula | ( | 500 | KVA x | 1000 | ) ÷ ( | 480 | SV x | 1.732 | ) = | 601 | FLA |  | Printout Service Transformer Step 1
| Transformer FLA - Formula | ( | 500 | KVA x | 1,000 | ) ÷ ( | 480 | SV x | 1.732 | ) = | 601 | FLA |  | Transformer FLA - Formula ( 500 KVA x 1,000 ) ÷ ( 480 SV x 1.732 ) = 601 FLA
|  | < | 500 | KVA | [9 empty] | < 500 KVA
Step 2 - Transformer Multiplier TM
| Transformer Multiplier TM - Formula | ( | 100 | ) ÷ ( | 0.9 | x | 3 | %Z ) = | 37.04 |  |  |  |  | Printout Service Transformer Step 2
| Transformer Multiplier TM - Formula | ( | 100 | ) ÷ ( | 0.9 | x | 3.0 | %Z ) = | 37.04 | TM |  |  |  | Transformer Multiplier TM - Formula ( 100 ) ÷ ( 0.9 x 3.0 %Z ) = 37.04 TM | [7 empty] | GENERAL | 0
[22 empty] | RIGID | 1
|  | Step 3A - Transformer Let-Through Current TLC | [19 empty] | EMT | 0
| Transformer Let-Through Current TLC - Formula | ((( | 601 | FLA x | 37.04 | TM ) x | 1 | UA ) + | 212 | MC ) = | 22473 | TLC |  | Printout Service Transformer Step 3 | [7 empty] | IMC | 0
| Transformer Let-Through Current TLC - Formula | ((( | 601 | FLA x | 37.04 | TM ) x | 1.0 | UA ) + | 212 | MC ) = | 22,473 | TLC |  | Transformer Let-Through Current TLC - Formula ((( 601 FLA x 37.04 TM ) x 1.0 UA ) + 212 MC ) = 22,473 TLC | [7 empty] | PVC-40 | 0
|  | Automatic/Manual | [8 empty] | 22,473 | TLC |  | 22,473 TLC | [7 empty] | RIGID/PVC | 0
[22 empty] | FLEX | 0
[11 empty] | 22.5 | K |  |  | 22.5 K | [6 empty] | LT-FLEX | 0
|  | Step 4 - Conductor Factor CF - Formula | [19 empty] | STELL=1 PLASTIC=2 | 1
|  | Three Phase | [19 empty] | CU=1 AL=2 | 0
| Conductor Factor CF - Formula | ( | 1.732 | x | 100 | L x | 22473 | TLC ) ÷ ( | #REF! | C x | #REF! | N x | 480 | SV ) = | #REF! | CF | Print
| Conductor Factor CF - Formula | ( | 1.732 | x | 100 | L x | 22,473 | TLC ) ÷ ( | #REF! | C x | #REF! | N x | 480 | SV ) = | #REF! | CF | #REF! |  |  |  |  | TOTAL | 1
Step 5 - Conductor Multiplier CM - Formula
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [6 empty] | Print
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [6 empty] | #REF!
1
Step 6 - Conductor Let-Through Current CLC - Formula
| Conductor Let-Through Current CLC - Formula | ( | 22473 | TLC x | #REF! | CM ) = | #REF! | CLC | [8 empty] | Print |  |  |  |  | 1 |  | 1 | 2 | 3 | 4
| Conductor Let-Through Current CLC - Formula | ( | 22,473 | TLC x | #REF! | CM ) = | #REF! | CLC |  |  | #REF! | [5 empty] | #REF! |  |  |  |  | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
[22 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single
|  |  |  | #REF! | [13 empty] | C7 | #REF! | #REF! |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL
[18 empty] | C8 |  |  | 1 | 389 | #14 | 389 | 389 | 237 | 237
[7 empty] | #REF! | K |  |  | #REF! | [6 empty] | C9 |  |  | 2 | 617 | #12 | 617 | 617 | 376 | 376
[18 empty] | C10 |  |  | 3 | 981 | #10 | 981 | 982 | 599 | 599
[18 empty] | C13 |  |  | 4 | 1557 | #8 | 1557 | 1559 | 951 | 952
%Z | - Transformer Impedance Value Nameplate %Z | [16 empty] | C14 |  |  | 5 | 2425 | #6 | 2425 | 2430 | 1481 | 1482
AFC | - Available Fault Current | [16 empty] | C15 |  |  | 6 | 3806 | #4 | 3806 | 3826 | 2346 | 2350
C | - Conductor Constant | [16 empty] | C16 |  |  | 7 | 4774 | #3 | 4774 | 4811 | 2952 | 2961
CF | - Conductor Factor | [19 empty] | 8 | 5907 | #2 | 5907 | 6044 | 3713 | 3730
CLC | - Conductor Let-Through Current | [18 empty] | #REF! | 9 | 7293 | #1 | 7293 | 7493 | 4645 | 4678
CM | - Conductor Multiplier | [19 empty] | 10 | 8925 | #1/0 | 8925 | 9317 | 5777 | 5838
FLA | - Transformer Full Load Amps | [19 empty] | 11 | 10755 | #2/0 | 10755 | 11424 | 7187 | 7301
KVA | - Kilovolt Amps | [19 empty] | 12 | 12844 | #3/0 | 12844 | 13923 | 8826 | 9110
L | - Length of Conductor | [19 empty] | 13 | 15082 | #4/0 | 15082 | 16673 | 10741 | 11174
MC | - Motor Short-Circuit Contribution | [19 empty] | 14 | 16483 | #250 | 16483 | 18594 | 12122 | 12862
N | - Number of Conductors Per Phase | [19 empty] | 15 | 18177 | #300 | 18177 | 20868 | 13910 | 14923
SV | - Secondary Voltage | [19 empty] | 16 | 19704 | #350 | 19704 | 22737 | 15484 | 16813
TLC | - Transformer Let-Through Current | [19 empty] | 17 | 20566 | #400 | 20566 | 24297 | 16671 | 18506
TM | - Transformer Multiplier | [19 empty] | 18 | 22185 | #500 | 22185 | 26706 | 18756 | 21391
UA | - Utility Adjustment 1.1 ( Voltages May Vary 10% )
V | - Voltage
[21 empty] | #REF! | #REF!
[23 empty] | C VALUES BUSWAY CU FEEDER |  |  |  |  | C VALUES BUSWAY CU PLUG-IN |  |  |  |  | C VALUES BUSWAY AL FEEDER
[18 empty] | C11 |  | 0 |  | 1 | 225 Amp | 18700 |  |  | 1 | 225 Amp | 28700 |  |  | 1 | 225 Amp | 23000
[18 empty] | C12 |  | 0 |  | 2 | 400 Amp | 23900 |  |  | 2 | 400 Amp | 38900 |  |  | 2 | 400 Amp | 34700
[18 empty] | C17 |  | 0 |  | 3 | 600 Amp | 36500 |  |  | 3 | 600 Amp | 41000 |  |  | 3 | 600 Amp | 38300
[22 empty] | 4 | 800 Amp | 49300 |  |  | 4 | 800 Amp | 46100 |  |  | 4 | 800 Amp | 57500
[22 empty] | 5 | 1000 Amp | 62900 |  |  | 5 | 1000 Amp | 69400 |  |  | 5 | 1000 Amp | 89300
[22 empty] | 6 | 1200 Amp | 76900 |  |  | 6 | 1200 Amp | 94300 |  |  | 6 | 1200 Amp | 97100
[22 empty] | 7 | 1350 Amp | 90100 |  |  | 7 | 1350 Amp | 119000 |  |  | 7 | 1350 Amp | 104200
[22 empty] | 8 | 1600 Amp | 101000 |  |  | 8 | 1600 Amp | 129900 |  |  | 8 | 1600 Amp | 120500
[22 empty] | 9 | 2000 Amp | 134200 |  |  | 9 | 2000 Amp | 142900 |  |  | 9 | 2000 Amp | 135100
[22 empty] | 10 | 2500 Amp | 180500 |  |  | 10 | 2500 Amp | 143800 |  |  | 10 | 2500 Amp | 156300
[22 empty] | 11 | 3000 Amp | 204100 |  |  | 11 | 3000 Amp | 144900 |  |  | 11 | 3000 Amp | 175400
[22 empty] | 12 | 4000 Amp | 277800
[26 empty] | #REF! | 1
100
[23 empty] | Steel Conduit |  |  | 1 | #14 Cable CU | #14 Cable CU | #14 Cable AL | AL | #14 Cable AL AL
[23 empty] | #REF! |  |  | 2 | #12 Cable CU | #12 Cable CU | #12 Cable AL | AL
[23 empty] | #REF! |  |  | 3 | #10 Cable CU | #10 Cable CU | #10 Cable AL | AL
[26 empty] | 4 | #8 Cable CU | #8 Cable CU | #8 Cable AL | AL
[26 empty] | 5 | #6 Cable CU | #6 Cable CU | #6 Cable AL | AL
[26 empty] | 6 | #4 Cable CU | #4 Cable CU | #4 Cable AL | AL
[26 empty] | 7 | #3 Cable CU | #3 Cable CU | #3 Cable AL | AL
[22 empty] | 1 | 1 Conductor(s) Per Phase |  |  | 8 | #2 Cable CU | #2 Cable CU | #2 Cable AL | AL
[22 empty] | 2 | 2 Conductor(s) Per Phase |  |  | 9 | #1 Cable CU | #1 Cable CU | #1 Cable AL | AL
[22 empty] | 3 | 3 Conductor(s) Per Phase |  |  | 10 | #1/0 Cable CU | #1/0 Cable CU | #1/0 Cable AL | AL
[22 empty] | 4 | 4 Conductor(s) Per Phase |  |  | 11 | #2/0 Cable CU | #2/0 Cable CU | #2/0 Cable AL | AL
[22 empty] | 5 | 5 Conductor(s) Per Phase |  |  | 12 | #3/0 Cable CU | #3/0 Cable CU | #3/0 Cable AL | AL
[22 empty] | 6 | 6 Conductor(s) Per Phase |  |  | 13 | #4/0 Cable CU | #4/0 Cable CU | #4/0 Cable AL | AL
[22 empty] | 7 | 7 Conductor(s) Per Phase |  |  | 14 | 250 MCM Cable CU | 250 MCM Cable CU | 250 MCM Cable AL | AL
[22 empty] | 8 | 8 Conductor(s) Per Phase |  |  | 15 | 300 MCM Cable CU | 300 MCM Cable CU | 300 MCM Cable AL | AL
[22 empty] | 9 | 9 Conductor(s) Per Phase |  |  | 16 | 350 MCM Cable CU | 350 MCM Cable CU | 350 MCM Cable AL | AL
[22 empty] | 10 | 10 Conductor(s) Per Phase |  |  | 17 | 400 MCM Cable CU | 400 MCM Cable CU | 400 MCM Cable AL | AL
[22 empty] | 11 | 11 Conductor(s) Per Phase |  |  | 18 | 500 MCM Cable CU | 500 MCM Cable CU | 500 MCM Cable AL | AL
[22 empty] | 12 | 12 Conductor(s) Per Phase |  |  | 19 | 600 MCM Cable CU | 600 MCM Cable CU | 600 MCM Cable AL | AL
[22 empty] | 13 | 13 Conductor(s) Per Phase |  |  | 20 | 750 MCM Cable CU | 750 MCM Cable CU | 750 MCM Cable AL | AL
[22 empty] | 14 | 14 Conductor(s) Per Phase |  |  | 21 | 1000 MCM Cable CU | 1000 MCM Cable CU | 1000 MCM Cable AL | AL
[22 empty] | 15 | 15 Conductor(s) Per Phase
[22 empty] | 16 | 16 Conductor(s) Per Phase |  |  | #REF!
[22 empty] | 17 | 17 Conductor(s) Per Phase
[22 empty] | 18 | 18 Conductor(s) Per Phase
[22 empty] | 19 | 19 Conductor(s) Per Phase
[22 empty] | 20 | 20 Conductor(s) Per Phase
#REF!

## Short 2 (hidden)
| MANUAL | MAIN TRANSFORMER
UTILITY TRANSFORMER INFINITE BUS
|  | Step 1 - Transformer FLA | [6 empty] | 3Y |  |  |  |  | AFC - Assumes Unlimited Primary Short-Circuit Current ( Infinite Bus )
|  | Three Phase | [11 empty] | ÷
| Transformer FLA - Formula | ( | 500 | KVA x | 1000 | ) ÷ ( | 480 | SV x | 1.732 | ) = | 601 | FLA |  | Printout Service Transformer Step 1
| Transformer FLA - Formula | ( | 500 | KVA x | 1,000 | ) ÷ ( | 480 | SV x | 1.732 | ) = | 601 | FLA |  | Transformer FLA - Formula ( 500 KVA x 1,000 ) ÷ ( 480 SV x 1.732 ) = 601 FLA
|  | < | 500 | KVA | [9 empty] | < 500 KVA
Step 2 - Transformer Multiplier TM
| Transformer Multiplier TM - Formula | ( | 100 | ) ÷ ( | 0.9 | x | 3 | %Z ) = | 37.04 |  |  |  |  | Printout Service Transformer Step 2
| Transformer Multiplier TM - Formula | ( | 100 | ) ÷ ( | 0.9 | x | 3.0 | %Z ) = | 37.04 | TM |  |  |  | Transformer Multiplier TM - Formula ( 100 ) ÷ ( 0.9 x 3.0 %Z ) = 37.04 TM | [7 empty] | GENERAL | 0
[22 empty] | RIGID | 0
|  | Step 3A - Transformer Let-Through Current TLC | [19 empty] | EMT | 1
| Transformer Let-Through Current TLC - Formula | ((( | 601 | FLA x | 37.04 | TM ) x | 1 | UA ) + | #REF! | MC ) = | #REF! | TLC |  | Printout Service Transformer Step 3 | [7 empty] | IMC | 0
| Transformer Let-Through Current TLC - Formula | ((( | 601 | FLA x | 37.04 | TM ) x | 1.0 | UA ) + | #REF! | MC ) = | #REF! | TLC |  | #REF! | [7 empty] | PVC-40 | 0
|  | Automatic/Manual | [8 empty] | #REF! | TLC |  | #REF! | [7 empty] | RIGID/PVC | 0
[22 empty] | FLEX | 0
[11 empty] | #REF! | K |  |  | #REF! | [6 empty] | LT-FLEX | 0
CONDUIT
|  | Step 4 - Conductor Factor CF - Formula | [19 empty] | STELL=1 PLASTIC=2 | 1
|  | Three Phase | [19 empty] | CU=1 AL=2 | 0
| Conductor Factor CF - Formula | ( | 1.732 | x | 30 | L x | #REF! | TLC ) ÷ ( | 22185 | C x | 0 | N x | 480 | SV ) = | #REF! | CF | Print
| Conductor Factor CF - Formula | ( | 1.732 | x | 30 | L x | #REF! | TLC ) ÷ ( | 22,185 | C x | 0 | N x | 480 | SV ) = | #REF! | CF | #REF! |  |  |  |  | TOTAL | 1
Step 5 - Conductor Multiplier CM - Formula
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [6 empty] | Print
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [6 empty] | #REF!
1
Step 6 - Conductor Let-Through Current CLC - Formula
| Conductor Let-Through Current CLC - Formula | ( | #REF! | TLC x | #REF! | CM ) = | #REF! | CLC | [8 empty] | Print |  |  |  |  | 1 |  | 1 | 2 | 3 | 4
| Conductor Let-Through Current CLC - Formula | ( | #REF! | TLC x | #REF! | CM ) = | #REF! | CLC |  |  | #REF! | [5 empty] | #REF! |  |  |  |  | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
[22 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single
|  |  |  | #REF! | [13 empty] | C7 | #500 | 18 |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL
[18 empty] | C8 |  |  | 1 | 389 | #14 | 389 | 389 | 237 | 237
[7 empty] | #REF! | K |  |  | #REF! | [6 empty] | C9 |  |  | 2 | 617 | #12 | 617 | 617 | 376 | 376
[18 empty] | C10 |  |  | 3 | 981 | #10 | 981 | 982 | 599 | 599
[18 empty] | C13 |  |  | 4 | 1557 | #8 | 1557 | 1559 | 951 | 952
%Z | - Transformer Impedance Value Nameplate %Z | [16 empty] | C14 |  |  | 5 | 2425 | #6 | 2425 | 2430 | 1481 | 1482
AFC | - Available Fault Current | [16 empty] | C15 |  |  | 6 | 3806 | #4 | 3806 | 3826 | 2346 | 2350
C | - Conductor Constant | [16 empty] | C16 |  |  | 7 | 4774 | #3 | 4774 | 4811 | 2952 | 2961
CF | - Conductor Factor | [19 empty] | 8 | 5907 | #2 | 5907 | 6044 | 3713 | 3730
CLC | - Conductor Let-Through Current | [18 empty] | 18 | 9 | 7293 | #1 | 7293 | 7493 | 4645 | 4678
CM | - Conductor Multiplier | [19 empty] | 10 | 8925 | #1/0 | 8925 | 9317 | 5777 | 5838
FLA | - Transformer Full Load Amps | [19 empty] | 11 | 10755 | #2/0 | 10755 | 11424 | 7187 | 7301
KVA | - Kilovolt Amps | [19 empty] | 12 | 12844 | #3/0 | 12844 | 13923 | 8826 | 9110
L | - Length of Conductor | [19 empty] | 13 | 15082 | #4/0 | 15082 | 16673 | 10741 | 11174
MC | - Motor Short-Circuit Contribution | [19 empty] | 14 | 16483 | #250 | 16483 | 18594 | 12122 | 12862
N | - Number of Conductors Per Phase | [19 empty] | 15 | 18177 | #300 | 18177 | 20868 | 13910 | 14923
SV | - Secondary Voltage | [19 empty] | 16 | 19704 | #350 | 19704 | 22737 | 15484 | 16813
TLC | - Transformer Let-Through Current | [19 empty] | 17 | 20566 | #400 | 20566 | 24297 | 16671 | 18506
TM | - Transformer Multiplier | [19 empty] | 18 | 22185 | #500 | 22185 | 26706 | 18756 | 21391
UA | - Utility Adjustment 1.1 ( Voltages May Vary 10% ) | [19 empty] | 19 | 22965 | #600 | 22965 | 28033 | 20093 | 23451
V | - Voltage | [19 empty] | 20 | 24137 | #750 | 24137 | 29735 | 21766 | 25976
[21 empty] | 21 | 25278 | #1000 | 25278 | 31491 | 23478 | 28779
[21 empty] | 22185 | #500
[21 empty] | 3000 A |  | C VALUES BUSWAY CU FEEDER | [5 empty] | C VALUES BUSWAY AL FEEDER
[18 empty] | C11 |  | 0 | [7 empty] | 1 | 225 Amp | 23000
[18 empty] | C12 |  | 0 | CU |  |  |  | COPPER | ALUMINUM |  |  | 2 | 400 Amp | 34700
[18 empty] | C17 |  | 0 | 11 | 1 | 225 A | 18700 | 18700 | 23000 |  |  | 3 | 600 Amp | 38300
[22 empty] | 2 | 400 A | 23900 | 23900 | 34700 |  |  | 4 | 800 Amp | 57500
[22 empty] | 3 | 600 A | 36500 | 36500 | 38300 |  |  | 5 | 1000 Amp | 89300
[22 empty] | 4 | 800 A | 49300 | 49300 | 57500 |  |  | 6 | 1200 Amp | 97100
[22 empty] | 5 | 1000 A | 62900 | 62900 | 89300 |  |  | 7 | 1350 Amp | 104200
[22 empty] | 6 | 1200 A | 76900 | 76900 | 97100 |  |  | 8 | 1600 Amp | 120500
[22 empty] | 7 | 1350 A | 90100 | 90100 | 104200 |  |  | 9 | 2000 Amp | 135100
[22 empty] | 8 | 1600 A | 101000 | 101000 | 120500 |  |  | 10 | 2500 Amp | 156300
[22 empty] | 9 | 2000 A | 134200 | 134200 | 135100 |  |  | 11 | 3000 Amp | 175400
[22 empty] | 10 | 2500 A | 180500 | 180500 | 156300
[22 empty] | 11 | 3000 A | 204100 | 204100 | 175400
[21 empty] | 204100 | 12 | 4000 A | 277800 | 277800 | 175400
[21 empty] | 22185 | CONDUIT

## Short 3 (hidden)
AUTO |  |  | Available Fault Current at Starting Point |  |  |  | 44903 | AFC
TRANSFORMER KNOWN AFC |  |  | Available Fault Current at Starting Point |  |  |  | 44,903 | AFC |  |  | 44,903 AFC | [7 empty] | Available Fault Current at Starting Point 44,903 AFC |  |  |  |  | 1
Step 4 - Calculated Factor F
|  | Three Phase | [21 empty] | 1 |  | 1 | 2 | 3 | 4
3Y | Conductor Factor CF - Formula | ( | 1.732 | x | 100 | L x | 19,969 | TLC ) ÷ ( | #REF! | C x | #REF! | N x | 480 | SV ) = | #REF! |  | CF | Print | [5 empty] | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
| Conductor Factor CF - Formula | ( | 1.732 | x | 100 | L x | 19,969 | TLC ) ÷ ( | #REF! | C x | #REF! | N x | 480 | SV ) = | #REF! |  | CF | #REF! | [5 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | [5 empty] | GENERAL | 0
[20 empty] | C7 | #REF! | #REF! |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL | [5 empty] | RIGID | 1
|  | Step 5 - Calculate M | [20 empty] | 1 | 389 | #14 | 389 | 389 | 237 | 237 | [5 empty] | EMT | 0
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [7 empty] | Print |  |  |  |  | 2 | 617 | #12 | 617 | 617 | 376 | 376 | [5 empty] | IMC | 0
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [7 empty] | #REF! |  |  |  |  | 3 | 981 | #10 | 981 | 982 | 599 | 599 | [5 empty] | PVC-40 | 0
[23 empty] | 4 | 1557 | #8 | 1557 | 1559 | 951 | 952 | [5 empty] | RIGID/PVC | 0
|  | Step 6 - Available Short Circuit (RMS Symmetrical) | [20 empty] | 5 | 2425 | #6 | 2425 | 2430 | 1481 | 1482 | [5 empty] | FLEX | 0
| Conductor Let-Through Current CLC - Formula | ( | 19,969 | TLC x | #REF! | CM ) = | #REF! | CLC | [9 empty] | Print |  |  |  |  | 6 | 3806 | #4 | 3806 | 3826 | 2346 | 2350 | [5 empty] | LT-FLEX | 0
| Conductor Let-Through Current CLC - Formula | ( | 19,969 | TLC x | #REF! | CM ) = | #REF! | CLC |  |  | #REF! | [6 empty] | #REF! |  |  |  |  | 7 | 4774 | #3 | 4774 | 4811 | 2952 | 2961
[23 empty] | 8 | 5907 | #2 | 5907 | 6044 | 3713 | 3730 | [5 empty] | STELL=1 PLASTIC=2 | 1
|  |  |  | #REF! | [17 empty] | #REF! | 9 | 7293 | #1 | 7293 | 7493 | 4645 | 4678 | [5 empty] | CU=1 AL=2 | 0
[23 empty] | 10 | 8925 | #1/0 | 8925 | 9317 | 5777 | 5838
|  | SECONDARY TRANSFORMER |  |  |  |  | #REF! | K |  |  | #REF! | [11 empty] | 11 | 10755 | #2/0 | 10755 | 11424 | 7187 | 7301 | [5 empty] | TOTAL | 1
[23 empty] | 12 | 12844 | #3/0 | 12844 | 13923 | 8826 | 9110
|  | Step A Calculate TF | [20 empty] | 13 | 15082 | #4/0 | 15082 | 16673 | 10741 | 11174
|  | ( | 44903 | AFC x | 13200 | PV x | 1.732 | x | 3 | %Z ) ÷ ( | 100000 | x | 500 | KVA ) = | 61.595 | [7 empty] | 14 | 16483 | #250 | 16483 | 18594 | 12122 | 12862
|  | ( | 44,903 | AFC x | 13200 | PV x | 1.732 | x | 3.0 | %Z ) ÷ ( | 100,000 | x | 500 | KVA ) = | 61.595 | TF |  | Calculate TF | Calculate TF ( 44,903 AFC x 13200 PV x 1.732 x 3.0 %Z ) ÷ ( 100,000 x 500 KVA ) = 61.595 TF |  |  |  | 15 | 18177 | #300 | 18177 | 20868 | 13910 | 14923
|  | Step B Calculate tM | [9 empty] | < | KVA | < 500 KVA | [8 empty] | 16 | 19704 | #350 | 19704 | 22737 | 15484 | 16813
|  | ( | 1 | ) / ( | 1 | + | 61.595 | TF ) = | 0.016 | TM | [12 empty] | 17 | 20566 | #400 | 20566 | 24297 | 16671 | 18506
|  | ( | 1 | ) / ( | 1 | + | 61.595 | TF ) = | 0.016 | TM | [7 empty] | Calculate TM | Calculate TM ( 1 ) / ( 1 + 61.595 TF ) = 0.016 TM |  |  |  | 18 | 22185 | #500 | 22185 | 26706 | 18756 | 21391
Step C Calculate TLC
|  | (((( | 13200 | PV ÷ | 480 | SV ) ÷ ( | 0.016 | TM x | 44903 | AFC )) x | 1 | UA ) + | 212 | MC ) = | 19969.3 | TLC
|  | (((( | 13,200 | PV ÷ | 480 | SV ) ÷ ( | 0.016 | TM x | 44,903 | AFC )) x | 1.0 | UA ) + | 212 | MC ) = | 19,969 | TLC |  | Calculate TLC | Calculate TLC (((( 13,200 PV ÷ 480 SV ) ÷ ( 0.016 TM x 44,903 AFC )) x 1.0 UA ) + 212 MC ) = 19,969 TLC
[11 empty] | 19,969 | TLC |  | 19,969 TLC
[23 empty] | #REF! | #REF!
|  |  |  | ÷ | [10 empty] | 20 | K |  |  | 20 K
[25 empty] | C VALUES BUSWAY CU FEEDER |  |  |  |  | C VALUES BUSWAY CU PLUG-IN |  |  |  |  | C VALUES BUSWAY AL FEEDER
[20 empty] | C11 |  | 0 | #REF! | 1 | 225 Amp | 18700 |  |  | 1 | 225 Amp | 28700 |  |  | 1 | 225 Amp | 23000
|  | (((( | 480 | PV ÷ | 208 | SV ) ÷ ( | 0.282 | TM x | 46,000 | AFC )) x | ua | UA ) + | mc | = | [5 empty] | C12 |  | 0 |  | 2 | 400 Amp | 23900 |  |  | 2 | 400 Amp | 38900 |  |  | 2 | 400 Amp | 34700
[20 empty] | C17 |  | 0 |  | 3 | 600 Amp | 36500 |  |  | 3 | 600 Amp | 41000 |  |  | 3 | 600 Amp | 38300
[24 empty] | 4 | 800 Amp | 49300 |  |  | 4 | 800 Amp | 46100 |  |  | 4 | 800 Amp | 57500
[24 empty] | 5 | 1000 Amp | 62900 |  |  | 5 | 1000 Amp | 69400 |  |  | 5 | 1000 Amp | 89300
[24 empty] | 6 | 1200 Amp | 76900 |  |  | 6 | 1200 Amp | 94300 |  |  | 6 | 1200 Amp | 97100
[24 empty] | 7 | 1350 Amp | 90100 |  |  | 7 | 1350 Amp | 119000 |  |  | 7 | 1350 Amp | 104200
[24 empty] | 8 | 1600 Amp | 101000 |  |  | 8 | 1600 Amp | 129900 |  |  | 8 | 1600 Amp | 120500
[24 empty] | 9 | 2000 Amp | 134200 |  |  | 9 | 2000 Amp | 142900 |  |  | 9 | 2000 Amp | 135100
|  | %Z | - Transformer Impedance Value Nameplate %Z | [20 empty] | 10 | 2500 Amp | 180500 |  |  | 10 | 2500 Amp | 143800 |  |  | 10 | 2500 Amp | 156300
|  | AFC | - Available Fault Current | [20 empty] | 11 | 3000 Amp | 204100 |  |  | 11 | 3000 Amp | 144900 |  |  | 11 | 3000 Amp | 175400
|  | C | - Conductor Constant | [20 empty] | 12 | 4000 Amp | 277800
|  | CF | - Conductor Factor
|  | CLC | - Conductor Let-Through Current | [24 empty] | #REF! | 1
|  | CM | - Conductor Multiplier | [21 empty] | 100
|  | KVA | - Kilovolt Amps | [21 empty] | Steel Conduit |  |  | 1 | #14 Cable CU | #14 Cable CU | #14 Cable AL | AL | #14 Cable AL AL
|  | L | - Length of Conductor | [21 empty] | #REF! |  |  | 2 | #12 Cable CU | #12 Cable CU | #12 Cable AL | AL
|  | MC | - Motor Short-Circuit Contribution | [21 empty] | #REF! |  |  | 3 | #10 Cable CU | #10 Cable CU | #10 Cable AL | AL
|  | N | - Number of Conductors Per Phase | [24 empty] | 4 | #8 Cable CU | #8 Cable CU | #8 Cable AL | AL
|  | PV | - Primary Voltage | [24 empty] | 5 | #6 Cable CU | #6 Cable CU | #6 Cable AL | AL
|  | SV | - Secondary Voltage | [24 empty] | 6 | #4 Cable CU | #4 Cable CU | #4 Cable AL | AL
|  | TF | - Transformer Factor | [24 empty] | 7 | #3 Cable CU | #3 Cable CU | #3 Cable AL | AL
|  | TLC | - Transformer Let-Through Current | [20 empty] | 1 | 1 Conductor(s) Per Phase |  |  | 8 | #2 Cable CU | #2 Cable CU | #2 Cable AL | AL
|  | TM | - Transformer Multiplier | [20 empty] | 2 | 2 Conductor(s) Per Phase |  |  | 9 | #1 Cable CU | #1 Cable CU | #1 Cable AL | AL
|  | UA | - Utility Adjustment 1.1 ( Voltages May Vary 10% ) | [20 empty] | 3 | 3 Conductor(s) Per Phase |  |  | 10 | #1/0 Cable CU | #1/0 Cable CU | #1/0 Cable AL | AL
[24 empty] | 4 | 4 Conductor(s) Per Phase |  |  | 11 | #2/0 Cable CU | #2/0 Cable CU | #2/0 Cable AL | AL
[24 empty] | 5 | 5 Conductor(s) Per Phase |  |  | 12 | #3/0 Cable CU | #3/0 Cable CU | #3/0 Cable AL | AL
[24 empty] | 6 | 6 Conductor(s) Per Phase |  |  | 13 | #4/0 Cable CU | #4/0 Cable CU | #4/0 Cable AL | AL
[24 empty] | 7 | 7 Conductor(s) Per Phase |  |  | 14 | 250 MCM Cable CU | 250 MCM Cable CU | 250 MCM Cable AL | AL
[24 empty] | 8 | 8 Conductor(s) Per Phase |  |  | 15 | 300 MCM Cable CU | 300 MCM Cable CU | 300 MCM Cable AL | AL
[24 empty] | 9 | 9 Conductor(s) Per Phase |  |  | 16 | 350 MCM Cable CU | 350 MCM Cable CU | 350 MCM Cable AL | AL
[24 empty] | 10 | 10 Conductor(s) Per Phase |  |  | 17 | 400 MCM Cable CU | 400 MCM Cable CU | 400 MCM Cable AL | AL
[24 empty] | 11 | 11 Conductor(s) Per Phase |  |  | 18 | 500 MCM Cable CU | 500 MCM Cable CU | 500 MCM Cable AL | AL
[24 empty] | 12 | 12 Conductor(s) Per Phase |  |  | 19 | 600 MCM Cable CU | 600 MCM Cable CU | 600 MCM Cable AL | AL
[24 empty] | 13 | 13 Conductor(s) Per Phase |  |  | 20 | 750 MCM Cable CU | 750 MCM Cable CU | 750 MCM Cable AL | AL
[24 empty] | 14 | 14 Conductor(s) Per Phase |  |  | 21 | 1000 MCM Cable CU | 1000 MCM Cable CU | 1000 MCM Cable AL | AL
[24 empty] | 15 | 15 Conductor(s) Per Phase
[24 empty] | 16 | 16 Conductor(s) Per Phase |  |  | #REF!
[24 empty] | 17 | 17 Conductor(s) Per Phase
[24 empty] | 18 | 18 Conductor(s) Per Phase
[24 empty] | 19 | 19 Conductor(s) Per Phase
[24 empty] | 20 | 20 Conductor(s) Per Phase
#REF!

## Short 4 (hidden)
MANUAL |  |  | Available Fault Current at Starting Point |  |  |  | 44903 | AFC
TRANSFORMER KNOWN AFC |  |  | Available Fault Current at Starting Point |  |  |  | 44,903 | AFC |  |  | 44,903 AFC | [7 empty] | Available Fault Current at Starting Point 44,903 AFC |  |  |  |  | 1
Step 4 - Calculated Factor F
|  | Three Phase | [8 empty] | CONDUIT | [12 empty] | 1 |  | 1 | 2 | 3 | 4
3Y | Conductor Factor CF - Formula | ( | 1.732 | x | 30 | L x | 19,969 | TLC ) ÷ ( | 22185 | C x | 1 | N x | 480 | SV ) = | 0.097 |  | CF | Print | [5 empty] | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
| Conductor Factor CF - Formula | ( | 1.732 | x | 30 | L x | 19,969 | TLC ) ÷ ( | 22,185 | C x | 1 | N x | 480 | SV ) = | 0.097 |  | CF | Conductor Factor CF - Formula ( 1.732 x 30 L x 19,969 TLC ) ÷ ( 22,185 C x 1 N x 480 SV ) = 0.097 CF | [5 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | GENERAL | 0
[20 empty] | C7 | #500 | 18 |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL | RIGID | 0
|  | Step 5 - Calculate M | [20 empty] | 1 | 389 | #14 | 389 | 389 | 237 | 237 | EMT | 1
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.097 | CF ) = | 0.912 | CM | [7 empty] | Print |  |  |  |  | 2 | 617 | #12 | 617 | 617 | 376 | 376 | IMC | 0
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.097 | CF ) = | 0.912 | CM | [7 empty] | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 0.097 CF ) = 0.912 CM |  |  |  |  | 3 | 981 | #10 | 981 | 982 | 599 | 599 | PVC-40 | 0
[23 empty] | 4 | 1557 | #8 | 1557 | 1559 | 951 | 952 | RIGID/PVC | 0
|  | Step 6 - Available Short Circuit (RMS Symmetrical) | [20 empty] | 5 | 2425 | #6 | 2425 | 2430 | 1481 | 1482 | FLEX | 0
| Conductor Let-Through Current CLC - Formula | ( | 19,969 | TLC x | 0.912 | CM ) = | 18212 | CLC | [9 empty] | Print |  |  |  |  | 6 | 3806 | #4 | 3806 | 3826 | 2346 | 2350 | LT-FLEX | 0
| Conductor Let-Through Current CLC - Formula | ( | 19,969 | TLC x | 0.912 | CM ) = | 18,212 | CLC |  |  | 18,212 CLC | [6 empty] | Conductor Let-Through Current CLC - Formula ( 19,969 TLC x 0.912 CM ) = 18,212 CLC |  |  |  |  | 7 | 4774 | #3 | 4774 | 4811 | 2952 | 2961
[23 empty] | 8 | 5907 | #2 | 5907 | 6044 | 3713 | 3730 | STELL=1 PLASTIC=2 | 1
|  |  |  | Conductor Let-Through Current CLC - Formula ( 19,969 TLC x 0.912 CM ) = 18,212 CLC | [17 empty] | 18 | 9 | 7293 | #1 | 7293 | 7493 | 4645 | 4678 | CU=1 AL=2 | 0
[23 empty] | 10 | 8925 | #1/0 | 8925 | 9317 | 5777 | 5838
|  | SECONDARY TRANSFORMER |  |  |  |  | 18.2 | K |  |  | 18.2 K | [11 empty] | 11 | 10755 | #2/0 | 10755 | 11424 | 7187 | 7301 | TOTAL | 1
[13 empty] | 3 | [9 empty] | 12 | 12844 | #3/0 | 12844 | 13923 | 8826 | 9110
|  | Step A Calculate TF | [20 empty] | 13 | 15082 | #4/0 | 15082 | 16673 | 10741 | 11174
|  | ( | 44903 | AFC x | 13200 | PV x | 1.732 | x | 3 | %Z ) ÷ ( | 100000 | x | 500 | KVA ) = | 61.595 | [7 empty] | 14 | 16483 | #250 | 16483 | 18594 | 12122 | 12862
|  | ( | 44,903 | AFC x | 13200 | PV x | 1.732 | x | 3.0 | %Z ) ÷ ( | 100,000 | x | 500 | KVA ) = | 61.595 | TF |  | Calculate TF | Calculate TF ( 44,903 AFC x 13200 PV x 1.732 x 3.0 %Z ) ÷ ( 100,000 x 500 KVA ) = 61.595 TF |  |  |  | 15 | 18177 | #300 | 18177 | 20868 | 13910 | 14923
|  | Step B Calculate tM | [9 empty] | < | KVA | < 500 KVA | [8 empty] | 16 | 19704 | #350 | 19704 | 22737 | 15484 | 16813
|  | ( | 1 | ) / ( | 1 | + | 61.595 | TF ) = | 0.016 | TM | [12 empty] | 17 | 20566 | #400 | 20566 | 24297 | 16671 | 18506
|  | ( | 1 | ) / ( | 1 | + | 61.595 | TF ) = | 0.016 | TM | [7 empty] | Calculate TM | Calculate TM ( 1 ) / ( 1 + 61.595 TF ) = 0.016 TM |  |  |  | 18 | 22185 | #500 | 22185 | 26706 | 18756 | 21391
|  | Step C Calculate TLC | [20 empty] | 19 | 22965 | #600 | 22965 | 28033 | 20093 | 23451
|  | (((( | 13200 | PV ÷ | 480 | SV ) ÷ ( | 0.016 | TM x | 44903 | AFC )) x | 1 | UA ) + | 212 | MC ) = | 19969 | TLC | [6 empty] | 20 | 24137 | #750 | 24137 | 29735 | 21766 | 25976
|  | (((( | 13,200 | PV ÷ | 480 | SV ) ÷ ( | 0.016 | TM x | 44,903 | AFC )) x | 1.0 | UA ) + | 212 | MC ) = | 19,969 | TLC |  | Calculate TLC | Calculate TLC (((( 13,200 PV ÷ 480 SV ) ÷ ( 0.016 TM x 44,903 AFC )) x 1.0 UA ) + 212 MC ) = 19,969 TLC |  |  |  | 21 | 25278 | #1000 | 25278 | 31491 | 23478 | 28779
[11 empty] | 19,969 | TLC |  | 19,969 TLC
[23 empty] | 22185 | #500
|  |  |  | ÷ | [10 empty] | 20 | K |  |  | 20 K
[20 empty] | C11 |  |  | 3000 A |  | C VALUES BUSWAY CU FEEDER
|  | (((( | 480 | PV ÷ | 208 | SV ) ÷ ( | 0.282 | TM x | 46,000 | AFC )) x | ua | UA ) + | mc | = | [5 empty] | C12
[20 empty] | C17 |  |  | CU |  |  |  | COPPER | ALUMINUM
[23 empty] | 11 | 1 | 225 A | 18700 | 18700 | 23000
[24 empty] | 2 | 400 A | 23900 | 23900 | 34700
[24 empty] | 3 | 600 A | 36500 | 36500 | 38300
[24 empty] | 4 | 800 A | 49300 | 49300 | 57500
[24 empty] | 5 | 1000 A | 62900 | 62900 | 89300
[24 empty] | 6 | 1200 A | 76900 | 76900 | 97100
|  | %Z | - Transformer Impedance Value Nameplate %Z | [20 empty] | 7 | 1350 A | 90100 | 90100 | 104200
|  | AFC | - Available Fault Current | [20 empty] | 8 | 1600 A | 101000 | 101000 | 120500
|  | C | - Conductor Constant | [20 empty] | 9 | 2000 A | 134200 | 134200 | 135100
|  | CF | - Conductor Factor | [20 empty] | 10 | 2500 A | 180500 | 180500 | 156300
|  | CLC | - Conductor Let-Through Current | [20 empty] | 11 | 3000 A | 204100 | 204100 | 175400
|  | CM | - Conductor Multiplier | [19 empty] | 204100 | 12 | 4000 A | 277800 | 277800 | 175400
|  | KVA | - Kilovolt Amps
|  | L | - Length of Conductor | [19 empty] | 22185 | CONDUIT
|  | MC | - Motor Short-Circuit Contribution
|  | N | - Number of Conductors Per Phase
|  | PV | - Primary Voltage
|  | SV | - Secondary Voltage
|  | TF | - Transformer Factor
|  | TLC | - Transformer Let-Through Current
|  | TM | - Transformer Multiplier
|  | UA | - Utility Adjustment 1.1 ( Voltages May Vary 10% )

## Short 5 (hidden)
| AUTO | NO TRANSFORMER
NO TRANSFORMER KNOWN AFC
|  |  | Available Fault Current at Starting Point |  |  | (( | 44903 | AFC x | 1 | UA ) + | 212 | MC ) = | 45115 | AFC
|  |  | Available Fault Current at Starting Point |  |  | (( | 44,903 | AFC x | 1.00 | UA ) + | 212 | MC ) = | 45,115 | AFC |  |  | Available Fault Current at Starting Point (( 44,903 AFC x 1.00 UA ) + 212 MC ) = 45,115 AFC
45,115 AFC
[13 empty] | 45.1 | K |  | 45.1 K
[22 empty] | GENERAL | 0
[22 empty] | RIGID | 1
[22 empty] | EMT | 0
[22 empty] | IMC | 0
[22 empty] | PVC-40 | 0
[22 empty] | RIGID/PVC | 0
[22 empty] | FLEX | 0
| 3Y | [20 empty] | LT-FLEX | 0
|  | Step 4 - Conductor Factor CF - Formula | [19 empty] | STELL=1 PLASTIC=2 | 1
|  | Three Phase | [19 empty] | CU=1 AL=2 | 0
| Conductor Factor CF - Formula | ( | 1.732 | x | 100 | L x | 45115 | AFC ) ÷ ( | #REF! | C x | #REF! | N x | 480 | SV ) = | #REF! | CF | Print
| Conductor Factor CF - Formula | ( | 1.732 | x | 100 | L x | 45,115 | AFC ) ÷ ( | #REF! | C x | #REF! | N x | 480 | SV ) = | #REF! | CF | #REF! |  |  |  |  | TOTAL | 1
Step 5 - Conductor Multiplier CM - Formula
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [6 empty] | Print
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #REF! | CF ) = | #REF! | CM | [6 empty] | #REF!
1
Step 6 - Conductor Let-Through Current CLC - Formula
| Conductor Let-Through Current CLC - Formula | ( | 45115 | AFC x | #REF! | CM ) = | #REF! | CLC | [8 empty] | Print |  |  |  |  | 1 |  | 1 | 2 | 3 | 4
| Conductor Let-Through Current CLC - Formula | ( | 45,115 | AFC x | #REF! | CM ) = | #REF! | CLC |  |  | #REF! | [5 empty] | #REF! |  |  |  |  | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
[22 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single
|  |  |  | #REF! | [13 empty] | C7 | #REF! | #REF! |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL
[21 empty] | 1 | 389 | #14 | 389 | 389 | 237 | 237
[7 empty] | #REF! | K |  |  | #REF! | [9 empty] | 2 | 617 | #12 | 617 | 617 | 376 | 376
[21 empty] | 3 | 981 | #10 | 981 | 982 | 599 | 599
[21 empty] | 4 | 1557 | #8 | 1557 | 1559 | 951 | 952
AFC | - Available Fault Current | [19 empty] | 5 | 2425 | #6 | 2425 | 2430 | 1481 | 1482
CF | - Conductor Factor | [19 empty] | 6 | 3806 | #4 | 3806 | 3826 | 2346 | 2350
C | - Conductor Constant | [19 empty] | 7 | 4774 | #3 | 4774 | 4811 | 2952 | 2961
N | - Number of Conductors Per Phase | [19 empty] | 8 | 5907 | #2 | 5907 | 6044 | 3713 | 3730
SV | - Secondary Voltage | [18 empty] | #REF! | 9 | 7293 | #1 | 7293 | 7493 | 4645 | 4678
CM | - Conductor Multiplier | [19 empty] | 10 | 8925 | #1/0 | 8925 | 9317 | 5777 | 5838
CLC | - Conductor Let-Through Current | [19 empty] | 11 | 10755 | #2/0 | 10755 | 11424 | 7187 | 7301
[21 empty] | 12 | 12844 | #3/0 | 12844 | 13923 | 8826 | 9110
[21 empty] | 13 | 15082 | #4/0 | 15082 | 16673 | 10741 | 11174
[21 empty] | 14 | 16483 | #250 | 16483 | 18594 | 12122 | 12862
[21 empty] | 15 | 18177 | #300 | 18177 | 20868 | 13910 | 14923
[21 empty] | 16 | 19704 | #350 | 19704 | 22737 | 15484 | 16813
[21 empty] | 17 | 20566 | #400 | 20566 | 24297 | 16671 | 18506
[21 empty] | 18 | 22185 | #500 | 22185 | 26706 | 18756 | 21391
[21 empty] | #REF! | #REF!
[23 empty] | C VALUES BUSWAY CU FEEDER |  |  |  |  | C VALUES BUSWAY CU PLUG-IN |  |  |  |  | C VALUES BUSWAY AL FEEDER
[18 empty] | C11 |  | 0 |  | 1 | 225 Amp | 18700 |  |  | 1 | 225 Amp | 28700 |  |  | 1 | 225 Amp | 23000
[18 empty] | C12 |  | 0 |  | 2 | 400 Amp | 23900 |  |  | 2 | 400 Amp | 38900 |  |  | 2 | 400 Amp | 34700
[18 empty] | C17 |  | 0 |  | 3 | 600 Amp | 36500 |  |  | 3 | 600 Amp | 41000 |  |  | 3 | 600 Amp | 38300
[22 empty] | 4 | 800 Amp | 49300 |  |  | 4 | 800 Amp | 46100 |  |  | 4 | 800 Amp | 57500
[22 empty] | 5 | 1000 Amp | 62900 |  |  | 5 | 1000 Amp | 69400 |  |  | 5 | 1000 Amp | 89300
[22 empty] | 6 | 1200 Amp | 76900 |  |  | 6 | 1200 Amp | 94300 |  |  | 6 | 1200 Amp | 97100
[22 empty] | 7 | 1350 Amp | 90100 |  |  | 7 | 1350 Amp | 119000 |  |  | 7 | 1350 Amp | 104200
[22 empty] | 8 | 1600 Amp | 101000 |  |  | 8 | 1600 Amp | 129900 |  |  | 8 | 1600 Amp | 120500
[22 empty] | 9 | 2000 Amp | 134200 |  |  | 9 | 2000 Amp | 142900 |  |  | 9 | 2000 Amp | 135100
[22 empty] | 10 | 2500 Amp | 180500 |  |  | 10 | 2500 Amp | 143800 |  |  | 10 | 2500 Amp | 156300
[22 empty] | 11 | 3000 Amp | 204100 |  |  | 11 | 3000 Amp | 144900 |  |  | 11 | 3000 Amp | 175400
[22 empty] | 12 | 4000 Amp | 277800
[26 empty] | #REF! | 1
100
[23 empty] | Steel Conduit |  |  | 1 | #14 Cable CU | #14 Cable CU | #14 Cable AL | AL | #14 Cable AL AL
[23 empty] | #REF! |  |  | 2 | #12 Cable CU | #12 Cable CU | #12 Cable AL | AL
[23 empty] | #REF! |  |  | 3 | #10 Cable CU | #10 Cable CU | #10 Cable AL | AL
[26 empty] | 4 | #8 Cable CU | #8 Cable CU | #8 Cable AL | AL
[26 empty] | 5 | #6 Cable CU | #6 Cable CU | #6 Cable AL | AL
[26 empty] | 6 | #4 Cable CU | #4 Cable CU | #4 Cable AL | AL
[26 empty] | 7 | #3 Cable CU | #3 Cable CU | #3 Cable AL | AL
[22 empty] | 1 | 1 Conductor(s) Per Phase |  |  | 8 | #2 Cable CU | #2 Cable CU | #2 Cable AL | AL
[22 empty] | 2 | 2 Conductor(s) Per Phase |  |  | 9 | #1 Cable CU | #1 Cable CU | #1 Cable AL | AL
[22 empty] | 3 | 3 Conductor(s) Per Phase |  |  | 10 | #1/0 Cable CU | #1/0 Cable CU | #1/0 Cable AL | AL
[22 empty] | 4 | 4 Conductor(s) Per Phase |  |  | 11 | #2/0 Cable CU | #2/0 Cable CU | #2/0 Cable AL | AL
[22 empty] | 5 | 5 Conductor(s) Per Phase |  |  | 12 | #3/0 Cable CU | #3/0 Cable CU | #3/0 Cable AL | AL
[22 empty] | 6 | 6 Conductor(s) Per Phase |  |  | 13 | #4/0 Cable CU | #4/0 Cable CU | #4/0 Cable AL | AL
[22 empty] | 7 | 7 Conductor(s) Per Phase |  |  | 14 | 250 MCM Cable CU | 250 MCM Cable CU | 250 MCM Cable AL | AL
[22 empty] | 8 | 8 Conductor(s) Per Phase |  |  | 15 | 300 MCM Cable CU | 300 MCM Cable CU | 300 MCM Cable AL | AL
[22 empty] | 9 | 9 Conductor(s) Per Phase |  |  | 16 | 350 MCM Cable CU | 350 MCM Cable CU | 350 MCM Cable AL | AL
[22 empty] | 10 | 10 Conductor(s) Per Phase |  |  | 17 | 400 MCM Cable CU | 400 MCM Cable CU | 400 MCM Cable AL | AL
[22 empty] | 11 | 11 Conductor(s) Per Phase |  |  | 18 | 500 MCM Cable CU | 500 MCM Cable CU | 500 MCM Cable AL | AL
[22 empty] | 12 | 12 Conductor(s) Per Phase |  |  | 19 | 600 MCM Cable CU | 600 MCM Cable CU | 600 MCM Cable AL | AL
[22 empty] | 13 | 13 Conductor(s) Per Phase |  |  | 20 | 750 MCM Cable CU | 750 MCM Cable CU | 750 MCM Cable AL | AL
[22 empty] | 14 | 14 Conductor(s) Per Phase |  |  | 21 | 1000 MCM Cable CU | 1000 MCM Cable CU | 1000 MCM Cable AL | AL
[22 empty] | 15 | 15 Conductor(s) Per Phase
[22 empty] | 16 | 16 Conductor(s) Per Phase |  |  | #REF!
[22 empty] | 17 | 17 Conductor(s) Per Phase
[22 empty] | 18 | 18 Conductor(s) Per Phase
[22 empty] | 19 | 19 Conductor(s) Per Phase
[22 empty] | 20 | 20 Conductor(s) Per Phase
#REF!

## Short 6 (hidden)
| MANUAL | NO TRANSFORMER
NO TRANSFORMER KNOWN AFC
|  |  | Available Fault Current at Starting Point |  |  | (( | 44903 | AFC x | 1 | UA ) + | 212 | MC ) = | 45115 | AFC
|  |  | Available Fault Current at Starting Point |  |  | (( | 44,903 | AFC x | 1.00 | UA ) + | 212 | MC ) = | 45,115 | AFC |  |  | Available Fault Current at Starting Point (( 44,903 AFC x 1.00 UA ) + 212 MC ) = 45,115 AFC
45,115 AFC
[13 empty] | 45.1 | K |  | 45.1 K
[22 empty] | GENERAL | 0
[22 empty] | RIGID | 0
[22 empty] | EMT | 1
[22 empty] | IMC | 0
[22 empty] | PVC-40 | 0
[22 empty] | RIGID/PVC | 0
[22 empty] | FLEX | 0
| 3Y | [20 empty] | LT-FLEX | 0
|  | Step 4 - Conductor Factor CF - Formula | [19 empty] | STELL=1 PLASTIC=2 | 1
|  | Three Phase | [8 empty] | CONDUIT | [10 empty] | CU=1 AL=2 | 0
| Conductor Factor CF - Formula | ( | 1.732 | x | 30 | L x | 45115 | AFC ) ÷ ( | 22185 | C x | 1 | N x | 480 | SV ) = | 0.22 | CF | Print
| Conductor Factor CF - Formula | ( | 1.732 | x | 30 | L x | 45,115 | AFC ) ÷ ( | 22,185 | C x | 1 | N x | 480 | SV ) = | 0.220 | CF | Conductor Factor CF - Formula ( 1.732 x 30 L x 45,115 AFC ) ÷ ( 22,185 C x 1 N x 480 SV ) = 0.220 CF |  |  |  |  | TOTAL | 1
Step 5 - Conductor Multiplier CM - Formula
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.22 | CF ) = | 0.82 | CM | [6 empty] | Print
| Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.220 | CF ) = | 0.820 | CM | [6 empty] | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 0.220 CF ) = 0.820 CM
1
Step 6 - Conductor Let-Through Current CLC - Formula
| Conductor Let-Through Current CLC - Formula | ( | 45115 | AFC x | 0.82 | CM ) = | 36994 | CLC | [8 empty] | Print |  |  |  |  | 1 |  | 1 | 2 | 3 | 4
| Conductor Let-Through Current CLC - Formula | ( | 45,115 | AFC x | 0.820 | CM ) = | 36,994 | CLC |  |  | 36,994 CLC | [5 empty] | Conductor Let-Through Current CLC - Formula ( 45,115 AFC x 0.820 CM ) = 36,994 CLC |  |  |  |  | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
[22 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single
|  |  |  | Conductor Let-Through Current CLC - Formula ( 45,115 AFC x 0.820 CM ) = 36,994 CLC | [13 empty] | C7 | #500 | 18 |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL
[21 empty] | 1 | 389 | #14 | 389 | 389 | 237 | 237
[7 empty] | 37 | K |  |  | 37 K | [9 empty] | 2 | 617 | #12 | 617 | 617 | 376 | 376
[21 empty] | 3 | 981 | #10 | 981 | 982 | 599 | 599
[21 empty] | 4 | 1557 | #8 | 1557 | 1559 | 951 | 952
AFC | - Available Fault Current | [19 empty] | 5 | 2425 | #6 | 2425 | 2430 | 1481 | 1482
CF | - Conductor Factor | [19 empty] | 6 | 3806 | #4 | 3806 | 3826 | 2346 | 2350
C | - Conductor Constant | [19 empty] | 7 | 4774 | #3 | 4774 | 4811 | 2952 | 2961
N | - Number of Conductors Per Phase | [19 empty] | 8 | 5907 | #2 | 5907 | 6044 | 3713 | 3730
SV | - Secondary Voltage | [18 empty] | 18 | 9 | 7293 | #1 | 7293 | 7493 | 4645 | 4678
CM | - Conductor Multiplier | [19 empty] | 10 | 8925 | #1/0 | 8925 | 9317 | 5777 | 5838
CLC | - Conductor Let-Through Current | [19 empty] | 11 | 10755 | #2/0 | 10755 | 11424 | 7187 | 7301
[21 empty] | 12 | 12844 | #3/0 | 12844 | 13923 | 8826 | 9110
[21 empty] | 13 | 15082 | #4/0 | 15082 | 16673 | 10741 | 11174
[21 empty] | 14 | 16483 | #250 | 16483 | 18594 | 12122 | 12862
[21 empty] | 15 | 18177 | #300 | 18177 | 20868 | 13910 | 14923
[21 empty] | 16 | 19704 | #350 | 19704 | 22737 | 15484 | 16813
[21 empty] | 17 | 20566 | #400 | 20566 | 24297 | 16671 | 18506
[21 empty] | 18 | 22185 | #500 | 22185 | 26706 | 18756 | 21391
[21 empty] | 19 | 22965 | #600 | 22965 | 28033 | 20093 | 23451
[21 empty] | 20 | 24137 | #750 | 24137 | 29735 | 21766 | 25976
[21 empty] | 21 | 25278 | #1000 | 25278 | 31491 | 23478 | 28779
[21 empty] | 22185 | #500
[21 empty] | 3000 A |  | C VALUES BUSWAY CU FEEDER
C11
[18 empty] | C12 |  |  | CU |  |  |  | COPPER | ALUMINUM
[18 empty] | C17 |  |  | 11 | 1 | 225 A | 18700 | 18700 | 23000
[22 empty] | 2 | 400 A | 23900 | 23900 | 34700
[22 empty] | 3 | 600 A | 36500 | 36500 | 38300
[22 empty] | 4 | 800 A | 49300 | 49300 | 57500
[22 empty] | 5 | 1000 A | 62900 | 62900 | 89300
[22 empty] | 6 | 1200 A | 76900 | 76900 | 97100
[22 empty] | 7 | 1350 A | 90100 | 90100 | 104200
[22 empty] | 8 | 1600 A | 101000 | 101000 | 120500
[22 empty] | 9 | 2000 A | 134200 | 134200 | 135100
[22 empty] | 10 | 2500 A | 180500 | 180500 | 156300
[22 empty] | 11 | 3000 A | 204100 | 204100 | 175400
[21 empty] | 204100 | 12 | 4000 A | 277800 | 277800 | 175400
[21 empty] | 22185 | CONDUIT