## Input
Residential 1-Line 2014 (Version 14.0A) - Dwelling Unit Calculation - Copyright 2014 - Durand & Associates | [8 empty] | MAIN | 0
PANEL
GENERAL INFORMATION
| PROJECT NAME |  | DEMO VERSION PROTECHED |  |  | SAMPLE |  | HIGH VOLTAGE | 240
| ADDRESS |  |  |  |  | 123 MAIN |  | LOW VOLTAGE | 120
| CITY/STATE/ZIP |  |  |  |  | FOLSOM, CA 95630 |  | PHASE | 3Y
ORANGE CELLS ARE PROTECTED IN DEMO VERSION
| PANEL NAME |  |  |  |  | DP | 0 |  | DP
| SELECT PHASE |  |  |  |  | 3Y | 0
| ENTER TOTAL SQUARE FOOTAGE |  |  |  |  | 1500 | 0
| APPLIANCE CIRCUITS ( 2 OR GREATER ) |  |  |  |  | 2 | 0
| LAUNDRY CIRCUITS ( ZERO OR GREATER ) |  |  |  |  | 1 | 0
FEEDER | [5 empty] | FEEDER
| FEEDER TYPE |  | SER |  |  | 1- SER CABLE | 0 | 0 | 0
| LENGTH |  | 50 |  |  | 4-#1 AL | 0 |  | 50 | ' | 50'
| WIRE CU/AL |  | AL |  |  | 1-#3 GND | 0
| WIRE TEMP |  | 75 |  |  |  | 0
| MINIMUM AMPS |  | 100 |  |  |  | 0
| % FACTOR |  | 0 |  |  |  | 0
|  |  | YES |  |  | AFC AT THIS PANEL | 0
|  |  | THW |  |  | 8,980 CLC | 0
|  |  | EMT |  |  |  | 0
MAJOR APPLIANCES
| DESCRIPTION |  | QTY | KVA (EA)
| RANGE(S) & OVEN(S) |  | 1 | 12 |  |  | 0 | 0 | 0
| CLOTHES DRYER(S) |  | 1 | 5 |  |  | 0 | 0 | 0 | 0
| WATER HEATER(S) |  | 1 | 2.5 |  |  | 0 | 0 | 0
HEATING/COOLING
1 | ENTER THE TOTAL NAMEPLATE RATING KVA OF AIR CONDITIONING |  |  |  |  | ENTER KVA
| AND COOLING EQUIPMENT. |  |  |  |  | 0 | 0
2 | ENTER THE TOTAL NAMEPLATE RATING(S) OF THE HEATING WHEN A HEAT |  |  |  |  | ENTER KVA
| PUMP IS USED WITHOUT ANY SUPPLEMENTAL ELECTRIC HEATING |  |  |  |  | 0 | 0
3 | ENTER THE TOTAL NAMEPLATE RATING KVA OF ELECTRIC THERMAL |  |  |  |  | ENTER KVA
| STORAGE AND OTHER HEATING SYSTEMS WHERE THE USUAL |  |  |  |  | 0 | 0
LOAD IS EXPECTED TO BE CONTINUOUS AT THE FULL NAMEPLATE
VALUE. SYSTEMS QUALIFYING UNDER THIS SECTION SHALL NOT
BE FIGURED UNDER ANY OTHER SECTION.
4 | ENTER 100% OF THE NAMEPLATE RATING(S) OF THE HEAT PUMP COMPRESSOR |  |  |  |  | ENTER KVA
| AND 65% OF THE SUPPLEMENTAL ELECTRIC HEATING FOR CENTRAL SPACE HEATING |  |  |  |  | 0 | 0
SYSTEMS. IF THE HEAT PUMP COMPRESSOR IS PREVENTED FROM OPERATING AT
THE SAME TIME AS THE SUPPLEMENTARY HEAT, IT DOES NOT NEED TO BE ADDED
TO THE SUPPLEMENTARY HEAT FOR THE TOTAL CENTRAL SPACE HEATING LOAD.
5 | ENTER THE TOTAL NAMEPLATE RATING KVA OF ALL ELECTRIC SPACE HEATING |  |  |  |  | ENTER KVA
| EQUIPMENT IF LESS THAN FOUR (4) SEPARATELY CONTROLLED UNITS. |  |  |  |  | 0 | 0
6 | ENTER THE TOTAL NAMEPLATE RATING KVA OF ALL ELECTRIC SPACE HEATING |  |  |  |  | ENTER KVA
| EQUIPMENT OF FOUR (4) OR MORE SEPARATELY CONTROLLED UNITS. |  |  |  |  | 9 | 0
MISC. 120 VOLT LOADS |  |  |  | AMPS |  |  | 0
|  | DESCRIPTION | QTY. | EACH
| 1 | DISHWASHER | 1 | 10 |  |  | 0 | 0 | 0 | 0
| 2 | [5 empty] | 0 | 0 | 0 | 0
| 3 | [5 empty] | 0 | 0 | 0 | 0
| 4 | [5 empty] | 0 | 0 | 0 | 0
| 5 | [5 empty] | 0 | 0 | 0 | 0
| 6 |  |  |  | ORANGE CELLS ARE PROTECTED IN DEMO VERSION |  | 0 | 0 | 0 | 0
| 7 | [5 empty] | 0 | 0 | 0 | 0
| 8 | [5 empty] | 0 | 0 | 0 | 0
| 9 | [5 empty] | 0 | 0 | 0 | 0
| 10 | [5 empty] | 0 | 0 | 0 | 0
| 11 | [5 empty] | 0 | 0 | 0 | 0
| 12 | [5 empty] | 0 | 0 | 0 | 0
| 13 | [5 empty] | 0 | 0 | 0 | 0
| 14 | [5 empty] | 0 | 0 | 0 | 0
| 15 | [5 empty] | 0 | 0 | 0 | 0
| 16 | [5 empty] | 0 | 0 | 0 | 0
| 17 | [5 empty] | 0 | 0 | 0 | 0
| 18 | [5 empty] | 0 | 0 | 0 | 0
| 19 | [5 empty] | 0 | 0 | 0 | 0
| 20 | [5 empty] | 0 | 0 | 0 | 0
| 21 | [5 empty] | 0 | 0 | 0 | 0
| 22 | [5 empty] | 0 | 0 | 0 | 0
| 23 | [5 empty] | 0 | 0 | 0 | 0
| 24 | [5 empty] | 0 | 0 | 0 | 0
MISC. 208 OR 240 VOLT LOADS |  |  |  | AMPS
|  | DESCRIPTION | QTY. | EACH | PHASE
| 1 |  |  |  | 3Y |  | 0 | 0 | 0 | 0 | 0
| 2 |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0
| 3 |  |  |  | 3Y |  | 0 | 0 | 0 | 0 | 0
| 4 |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0
| 5 |  |  |  | 3Y |  | 0 | 0 | 0 | 0 | 0
| 6 |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0
| 7 |  |  |  | 3Y |  | 0 | 0 | 0 | 0 | 0
| 8 |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0
| 9 |  |  |  | 3Y |  | 0 | 0 | 0 | 0 | 0
| 10 |  |  |  | 1 |  | 0 | 0 | 0 | 0 | 0
Residential 1-Line 2014 (Version 14.0A) - Dwelling Unit Calculation - Copyright 2014 - Durand & Associates
0

## Calcs
(
SINGLE FAMILY SERVICE LOAD CALCULATIONS |  |  |  | PROJECT NAME |  |  |  | SAMPLE |  | 0 |  |  |  |  | TOTAL SQ FOOTAGE ( |  |  |  |  | MISC LOADS
BASED ON THE 2008 NEC SECTION 220.82 |  |  |  | DWELLING UNIT |  |  |  | DP |  | 0 |  |  |  |  | APPLIANCE CIRCUITS ( |  |  |  | 1 | DISHWASHER | 1 | X | 10 | A X | 120 | V ) = | DISHWASHER ( 1 X 10A X 120 V ) = |  | 1200
[15 empty] | LAUNDRY CIRCUITS ( |  |  |  | 2 |  | 0 | X | 0 | A X | 120 | V ) =
GENERAL LOADS NEC 220.82(B) |  |  |  | NEUTRAL LOAD NEC 220.61 | [14 empty] | 3 |  | 0 | X | 0 | A X | 120 | V ) =
TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  |  | 4500 | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  |  |  |  | 4500 |  | 1,500 | SQ FT X 3 VA ) = |  |  | TOTAL SQ FOOTAGE ( 1,500 SQ FT X 3 VA ) = |  |  |  | 4 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | RANGES | 1
APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  |  | 3000 | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  |  |  |  | 3000 |  | 2 | X 1,500 VA ) = |  |  | APPLIANCE CIRCUITS ( 2 X 1,500 VA ) = |  |  |  | 5 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | SIZE | 12
LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  |  | 1500 | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  |  |  |  | 1500 |  | 1 | X 1,500 VA ) = |  |  | LAUNDRY CIRCUITS ( 1 X 1,500 VA ) = |  |  |  | 6 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | PHASE | 3Y
|  |  |  | TOTAL CONNECTED NEUTRAL LOAD |  |  |  |  | 9000 |  | 1 | X | 12,000 | VA = | 1 X 12,000 VA = |  |  |  | 7 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | CEILING | 2
RANGE ( 2 ON ANY 2 PHASES ) = 24,000 KVA | [10 empty] | 1 | X | 5,000 | VA = | 1 X 5,000 VA = |  |  |  | 8 |  | 0 | X | 0 | A X | 120 | V ) =
PER PHASE DEMAND ( 24,000 VA ÷ 2 ) = 12,000 VA |  |  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = |  |  |  |  | 3000 |  | 1 | X | 2,500 | VA ) = | WATER HEATERS (1 X 2,500 VA ) = |  |  |  | 9 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | RANGE ( | 2 | ON ANY 2 PHASES ) = | 24000 | KVA
EQUIVALENT 3-PHASE LOAD ( 12,000 VA X 3 ) = |  |  | 36000 | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = |  |  |  |  | 2100 | [9 empty] | 10 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | RANGE ( | 2 | ON ANY 2 PHASES ) = | 24,000 | KVA |  | RANGE ( 2 ON ANY 2 PHASES ) = 24,000 KVA
|  |  |  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = |  |  |  |  | 0 | [5 empty] | WATER HEATERS ( |  |  |  | 11 |  | 0 | X | 0 | A X | 120 | V ) =
DRYER ( 2 ON ANY 2 PHASES ) = 10,000 KVA |  |  |  | SUBTOTAL |  |  |  |  | 5100 | [9 empty] | 12 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | PER PHASE DEMAND ( | 24000 | VA ÷ 2 ) = | 12000 | VA
PER PHASE DEMAND ( 10,000 VA ÷ 2 ) = 5,000 VA | [18 empty] | 13 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | PER PHASE DEMAND ( | 24,000 | VA ÷ 2 ) = | 12,000 | VA |  | PER PHASE DEMAND ( 24,000 VA ÷ 2 ) = 12,000 VA
EQUIVALENT 3-PHASE LOAD ( 5,000 VA X 3 ) = |  |  | 15000 | RANGE DEMAND NEC 220.61 | [14 empty] | 14 |  | 0 | X | 0 | A X | 120 | V ) =
|  |  |  | PROHIBITED REDUCTION NEC 220.61(C)(1) | [6 empty] | MISC LOADS | 1200 | [6 empty] | 15 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | EQUIVALENT 3-PHASE LOAD ( | 12000 | VA X 3 ) = |  | 36000
WATER HEATERS (1 X 2,500 VA ) = |  |  | 2500 | 100% OF TABLE 220.55 ( 8,000 VA X 1.00 ) = |  |  |  |  | 8000 | [9 empty] | 16 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | EQUIVALENT 3-PHASE LOAD ( | 12,000 | VA X 3 ) = |  |  |  | EQUIVALENT 3-PHASE LOAD ( 12,000 VA X 3 ) =
[19 empty] | 17 |  | 0 | X | 0 | A X | 120 | V ) =
MISC LOADS NEC 220.82(B)(4) |  |  |  | DRYER DEMAND NEC 220.61 | [14 empty] | 18 |  | 0 | X | 0 | A X | 120 | V ) =
DISHWASHER ( 1 X 10A X 120 V ) = |  |  | 1200 | PROHIBITED REDUCTION NEC 220.61(C)(1) | [14 empty] | 19 |  | 0 | X | 0 | A X | 120 | V ) =
|  |  |  | 100% OF TABLE 220.54 ( 5,000 VA 1.00 VA X 1.00 ) = |  |  |  |  | 5000 | [9 empty] | 20 |  | 0 | X | 0 | A X | 120 | V ) =
[19 empty] | 21 |  | 0 | X | 0 | A X | 120 | V ) =
|  |  |  | UNBALANCED MISC LOADS |  |  |  |  | 1200 | [9 empty] | 22 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | DRYERS | 1
[19 empty] | 23 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | SIZE | 5
|  |  |  | NEUTRAL LOAD VA |  |  |  |  | 19300 | [9 empty] | 24 |  | 0 | X | 0 | A X | 120 | V ) = | [6 empty] | PHASE | 3Y
[19 empty] | 25 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [6 empty] | CEILING | 2 |  |  |  | 20000
|  |  |  | NEUTRAL LOAD ( 19,300 VA ÷ 1.732 ÷ 240 V ) = |  |  |  |  | 46 |  | FIRST 200 A @ 100% ( | 46 | A X 1.00 ) = | [5 empty] | 26 |  | 0 | X | 0 | A X | 240 | V ) =
[11 empty] | FIRST 200 A @ 100% ( | 46 | A X 1.00 ) = | FIRST 200 A @ 100% (46 A X 1.00 ) = |  |  |  |  | 27 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [6 empty] | DRYER ( | 2 | ON ANY 2 PHASES ) = | 10000 | KVA
|  |  |  | FURTHER DEMAND FACTOR - 2005 NEC 220.61(B)(2) | [14 empty] | 28 |  | 0 | X | 0 | A X | 240 | V ) = | [6 empty] | DRYER ( | 2 | ON ANY 2 PHASES ) = | 10,000 | KVA |  | DRYER ( 2 ON ANY 2 PHASES ) = 10,000 KVA
|  |  |  | FIRST 200 A @ 100% (46 A X 1.00 ) = |  |  |  |  | 46 |  | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | [5 empty] | 29 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) =
|  |  |  | REMAINDER @ 70% ( 0 A X 0.70 ) = |  |  |  |  | 0 |  | REMAINDER @ 70% ( | 0 | A X 0.70 ) = | REMAINDER @ 70% ( 0 A X 0.70 ) = |  |  |  |  | 30 |  | 0 | X | 0 | A X | 240 | V ) = | [6 empty] | PER PHASE DEMAND ( | 10000 | VA ÷ 2 ) = | 5000 | VA
[19 empty] | 31 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [6 empty] | PER PHASE DEMAND ( | 10,000 | VA ÷ 2 ) = | 5,000 | VA |  | PER PHASE DEMAND ( 10,000 VA ÷ 2 ) = 5,000 VA
|  |  |  | MINIMUM NEUTRAL CONDUCTOR AMPACITY |  |  |  |  | 46 | [9 empty] | 32 |  | 0 | X | 0 | A X | 240 | V ) =
[19 empty] | 33 |  | 0 | X | 0 | A X 1.732 X | 240 | V ) = | [6 empty] | EQUIVALENT 3-PHASE LOAD ( | 5000 | VA X 3 ) = |  | 15000
[19 empty] | 34 |  | 0 | X | 0 | A X | 240 | V ) = | [6 empty] | EQUIVALENT 3-PHASE LOAD ( | 5,000 | VA X 3 ) = |  |  |  | EQUIVALENT 3-PHASE LOAD ( 5,000 VA X 3 ) =
VOLTAGE DROP CALCULATIONS
( 2 X 50' L X 0.2530 R X 84.0 A ÷ 1,000 X 0.866 ) = 1.8 VD
( 1.8 VD ÷ 240 V X 100 ) = 0.8 % VD
FAULT CURRENT CALCULATIONS
(( 28,875 AFC X 1.00 UA ) + 0 MC ) = 28,875 AFC
( 1.732 X 50 L X 28,875 AFC ) ÷ ( 4,699 C X 1 N X 240 V ) = 2.217 CF
( 1 ) ÷ ( 1 + 2.217 CF ) = 0.311 CM
( 28,875 AFC X 0.311 CM ) = 8,980 CLC
MAIN
PANEL
100A-3P
- FEEDER PER TABLE 310.16 - 75° C
TOTAL GENERAL LOAD |  |  | 63700 |  |  |  | 50'
FIRST 10 KVA AT 100% |  |  | 10000 |  |  |  | 1- SER CABLE
REMAINDER OF LOAD AT 40% |  |  | 21480 |  |  |  | 4-#1 AL
SUB TOTAL GENERAL LOAD |  |  | 31480 |  |  |  | 1-#3 GND
HEATING & COOLING LOADS - NEC 220.82(C)
(1) AC LOAD ( 0 VA X 100% ) = 0 VA
(2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA
(3) ELECTRIC CONTINUOUS ( 0 VA X 100% ) = 0 VA
(4) HEAT PUMPS WITH SUPPL ( 0 VA X 100% ) = 0 VA
(5) SPACE HEATING ( 0 VA X 65% ) = 0 VA |  |  |  |  | DWELLING
(6) SPACE HEATING (9,000 VA X 40% ) = 9,000 VA |  |  |  |  | PANEL
LARGEST HEATING OR COOLING LOAD |  |  | 3600 |  | DP
TOTAL KVA |  |  | 35080
TOTAL AMPS ( 35,080 VA ÷ 1.732 ÷ 240 V ) = |  |  | 84
FUTURE AMPS ( 0% ) |  |  | 0
DESIGN AMPS |  |  | 84
KEY | (N) - Neutral | VD - Voltage Drop
A - Amps
L - Length
R - Resistance
V - Volts
VA - Volt Amps
TEXT
Prepared With Residential 1-Line 2014 Software - Copyright Durand & Associates | [19 empty] | (1) AC LOAD ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (1) AC LOAD ( 0 VA X 100% ) = 0 VA | 0
[20 empty] | (2) HEAT PUMPS NO SUPP ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (2) HEAT PUMPS NO SUPP ( 0 VA X 100% ) = 0 VA | 0
[20 empty] | (3) ELECTRIC CONTINUOUS ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (3) ELECTRIC CONTINUOUS ( 0 VA X 100% ) = 0 VA | 0
[20 empty] | (4) HEAT PUMPS WITH SUPPL ( |  |  |  | VA | 0 | 0 | VA X 100% ) = | (4) HEAT PUMPS WITH SUPPL ( 0 VA X 100% ) = 0 VA | 0
[20 empty] | (5) SPACE HEATING ( |  |  |  | VA | 0 | 0 | VA X 65% ) = | (5) SPACE HEATING ( 0 VA X 65% ) = 0 VA | 0
[20 empty] | (6) SPACE HEATING ( |  |  |  | VA | 9000 | 9,000 | VA X 40% ) = | (6) SPACE HEATING (9,000 VA X 40% ) = 9,000 VA | 3600
3600
[20 empty] | 35080 |  |  |  |  | 35,080 | VA ÷ 1.732 ÷ | 240 | V ) = | 84 |  |  | =
[25 empty] | TOTAL AMPS ( |  |  | TOTAL AMPS ( 35,080 VA ÷ 1.732 ÷ 240 V ) =
NEUTRAL
[19 empty] | FIRST 3,000 VA @ 100% ( | 3000 |  | 3,000 | VA X 1.00 ) = |  |  |  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) =
[19 empty] | 3,000-120,000 VA @ 35% ( | 9000 |  | 3000 | 6000 | 6,000 | VA X 0.35 ) = |  |  | 3,000-120,000 VA @ 35% ( 6,000 VA X 0.35 ) = | 2100
[19 empty] | OVER 120,000 VA @ 25% ( | 0 |  |  | 0 |  | VA X 0.25 ) = |  |  | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = | 0
RANGE
[19 empty] | 100% OF TABLE 220.55 ( | 8000 |  |  | 8,000 |  | VA X 1.00 ) = |  |  | 100% OF TABLE 220.55 ( 8,000 VA X 1.00 ) = | 8000
[20 empty] | DRYER |  |  |  | 1
[19 empty] | 100% OF TABLE 220.54 ( | 5000 |  |  | 5,000 | 1.00 | VA X 1.00 ) = | VA |  | 100% OF TABLE 220.54 ( 5,000 VA 1.00 VA X 1.00 ) = | 5000 | 5000 | 3500
UNBALANCED
[20 empty] | 1200 |  |  | 1,200 |  | VA X 1.00 = |  |  | 1,200 VA X 1.00 = | 1200
NEUTRAL AMPS
[19 empty] | NEUTRAL LOAD ( | 19300 |  |  | 19,300 |  | VA ÷ 1.732 ÷ | 240 | V ) = | NEUTRAL LOAD ( 19,300 VA ÷ 1.732 ÷ 240 V ) = |  | 46
1
[11 empty] | VD | 2
[11 empty] | AFC | [8 empty] | FUTUR AMPS (
[20 empty] | 84 |  |  | 84 |  | A X | 0 | = | 84 A X 0 =
[23 empty] | FUTURE AMPS |  | ( | 0 | % ) | FUTURE AMPS ( 0% )
[12 empty] | 2 |  | 1 |  | 2 | 3 | 4
[12 empty] | (N) - Neutral |  | (N) - Neutral |  | (N) - Neutral | (N) - Neutral | (N) - Neutral
[12 empty] | A - Amps |  | A - Amps |  | A - Amps | A - Amps | A - Amps
[12 empty] | L - Length |  | VA - Volt Amps |  | L - Length | AFC - Available Fault Current | AFC - Available Fault Current
[12 empty] | R - Resistance |  |  |  | R - Resistance | AL - Aluminum | AL - Aluminum
[12 empty] | V - Volts |  |  |  | V - Volts | C - Conductor Constance | C - Conductor Constance
[12 empty] | VA - Volt Amps |  |  |  | VA - Volt Amps | CF - Conductor Factor | CF - Conductor Factor
[12 empty] | VD - Voltage Drop |  |  |  | VD - Voltage Drop | CLC - Conductor Let Through Current | CLC - Conductor Let Through Current
[17 empty] | CM - Conductor Multiplier | CM - Conductor Multiplier
[17 empty] | CU - Copper | CU - Copper
[17 empty] | GND - Ground | GND - Ground
[17 empty] | L - Length | L - Length
[17 empty] | MC - Motor Contribution | MC - Motor Contribution
[17 empty] | N - Number of Conductors | N - Number of Conductors
[17 empty] | UA - Utility Adjustment | R - Resistance
[17 empty] | V - Volts | UA - Utility Adjustment
[17 empty] | VA - Volt Amps | V - Volts
VA - Volt Amps
VD - Voltage Drop

## Tables (hidden)
TABLE 220.55, FROM 2005 N.E.C.
|  | NUMBER |  |  | COLUMN C |  | COLUMN A |  | COLUMN B
|  | OF |  |  | NOT OVER 12 |  | LESS THAN 3.5 |  | 3.5 to 8.75
|  | APPLIANCES |  |  | KW RATING |  | KW RATING |  | KW RATING
|  | 1 | 1 | 8 | 8 | 0.8 | 80 | 0.8 | 80
NUMBER OF RANGES | 1 | 2 | 2 | 0 | 11 | 0 | 75 | 0 | 65
|  | 3 | 3 | 0 | 14 | 0 | 70 | 0 | 55
MAXIMUM DEMAND |  | 4 | 4 | 0 | 17 | 0 | 66 | 0 | 50
FROM COLUMN A |  | 5 | 5 | 0 | 20 | 0 | 62 | 0 | 45
TABLE 220-19 | 8 | 6 | 6 | 0 | 21 | 0 | 59 | 0 | 43
|  | 7 | 7 | 0 | 22 | 0 | 56 | 0 | 40
PERCENTAGE DEMAND |  | 8 | 8 | 0 | 23 | 0 | 53 | 0 | 36
FROM COLUMN B |  | 9 | 9 | 0 | 24 | 0 | 51 | 0 | 35
TABLE 220.55 | 0.8 | 10 | 10 | 0 | 25 | 0 | 49 | 0 | 34
|  | 11 | 11 | 0 | 26 | 0 | 47 | 0 | 32
PERCENTAGE DEMAND |  | 12 | 12 | 0 | 27 | 0 | 45 | 0 | 32
FROM COLUMN C |  | 13 | 13 | 0 | 28 | 0 | 43 | 0 | 32
TABLE 220.55 | 0.8 | 14 | 14 | 0 | 29 | 0 | 41 | 0 | 32
|  | 15 | 15 | 0 | 30 | 0 | 40 | 0 | 32
|  | 16 | 16 | 0 | 31 | 0 | 39 | 0 | 28
|  | 17 | 17 | 0 | 32 | 0 | 38 | 0 | 28
|  | 18 | 18 | 0 | 33 | 0 | 37 | 0 | 28
|  | 19 | 19 | 0 | 34 | 0 | 36 | 0 | 28
|  | 20 | 20 | 0 | 35 | 0 | 35 | 0 | 28
|  | 21 | 21 | 0 | 36 | 0 | 34 | 0 | 26
|  | 22 | 22 | 0 | 37 | 0 | 33 | 0 | 26
|  | 23 | 23 | 0 | 38 | 0 | 32 | 0 | 26
|  | 24 | 24 | 0 | 39 | 0 | 31 | 0 | 26
|  | 25 | 25 | 0 | 40 | 0 | 30 | 0 | 26
|  | 26-30 | 26 | 0 | 15 KW + 1KW | 0 | 30 | 0 | 24
|  | 31-40 | 31 |  | FOR EACH RANGE |  | 30 | 0 | 22
|  | 41-50 | 41 | 0 | 25 KW + .75 KW |  | 30 | 0 | 20
|  | 51-60 | 51 |  | FOR EACH |  | 30 | 0 | 18
|  | 61 & OVER | 61 |  | RANGE |  | 30 | 0 | 16
|  |  |  | 8 |  | 0.8 |  | 0.8
TABLE 220.54, FROM 2005 N.E.C.
|  | NUMBER |  |  | DEMAND
|  | OF |  |  | FACTOR
|  | DRYERS |  |  | PERCENT
NUMBER OF DRYERS | 1 | 1 | 1 | 100 | 100
|  | 2 | 2 | 0 | 100
DEMAND FACTOR | 100 | 3 | 3 | 0 | 100
|  | 4 | 4 | 0 | 100
| 15000 | 5 | 5 | 0 | 85
|  | 6 | 6 | 0 | 75
| 15000 | 7 | 7 | 0 | 65
|  | 8 | 8 | 0 | 60
|  | 9 | 9 | 0 | 55
|  | 10 | 10 | 0 | 50
|  | 11 | 11 | 0 | 47
|  | 12 | 12 | 0 | 46 |  | 46 | 46 | 0
|  | 13 | 13 | 0 | 45 |  | 45 | 45 | 0
|  | 14 | 14 | 0 | 44 |  | 44 | 44 | 0
|  | 15 | 15 | 0 | 43 |  | 43 | 43 | 0
|  | 16 | 16 | 0 | 42 |  | 42 | 42 | 0
|  | 17 | 17 | 0 | 41 |  | 41 | 41 | 0
|  | 18 | 18 | 0 | 40 |  | 40 | 40 | 0
|  | 19 | 19 | 0 | 39 |  | 39 | 39 | 0
|  | 20 | 20 | 0 | 38 |  | 38 | 38 | 0
|  | 21 | 21 | 0 | 37 |  | 37 | 37 | 0
|  | 22 | 22 | 0 | 36 |  | 36 | 36 | 0
|  | 23 | 23 | 0 | 35 |  | 35 | 35 | 0
|  | 24 | 24 | 0 | 34.5 |  | 34.5 | 34.5 | 0
|  | 25 | 25 | 0 | 34 |  | 34 | 34 | 0
|  | 26 | 26 | 0 | 33.5 |  | 33.5 | 33.5 | 0
|  | 27 | 27 | 0 | 33 |  | 33 | 33 | 0
|  | 28 | 28 | 0 | 32.5 |  | 32.5 | 32.5 | 0
|  | 29 | 29 | 0 | 32 |  | 32 | 32 | 0
|  | 30 | 30 | 0 | 31.5 |  | 31.5 | 31.5 | 0
|  | 31 | 31 | 0 | 31 |  | 31 | 31 | 0
|  | 32 | 32 | 0 | 30.5 |  | 30.5 | 30.5 | 0
|  | 33 | 33 | 0 | 30 |  | 30 | 30 | 0
|  | 34 | 34 | 0 | 29.5 |  | 29.5 | 29.5 | 0
|  | 35 | 35 | 0 | 29 |  | 29 | 29 | 0
|  | 36 | 36 | 0 | 28.5 |  | 28.5 | 28.5 | 0
|  | 37 | 37 | 0 | 28 |  | 28 | 28 | 0
|  | 38 | 38 | 0 | 27.5 |  | 27.5 | 27.5 | 0
|  | 39 | 39 | 0 | 27 |  | 27 | 27 | 0
|  | 40 | 40 | 0 | 26.5 |  | 26.5 | 26.5 | 0
|  | 41 | 41 | 0 | 26 |  | 26 | 26 | 0
|  | 42 | 42 | 0 | 25.5 |  | 25.5 | 25.5 | 0
|  | 43 & OVER | 43 | 0 | 25 |  | 25 |  | 99
100
RANGE ADD
5% PER KVA
OVER 12
| RANGE RATING | 12 | KVA
0
| 12 | 13 | 0.05
| 13 | 14 | 0.1
| 14 | 15 | 0.15
| 15 | 16 | 0.2
| 16 | 17 | 0.25
| 17 | 18 | 0.3
| 18 | 19 | 0.35
| 19 | 20 | 0.4
| 20 | 21 | 0.45
| 21 | 22 | 0.5
| 22 | 23 | 0.55
| 23 | 24 | 0.6
| 24 | 25 | 0.65
| 25 | 26 | 0.7
| 26 | 27 | 0.75
3Y
UNBALANCED LOAD
LOAD
| 1 | 1200 |  |  |  | 1200
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
|  | 1200 | 0 |  |  | 1200 | 0 | 0
1200
1200

## Conduit (hidden)
# OF CONDUITS
|  | 1 1/2'' |  | EMT | ( | 4 | - | #1 |  |  | 1 | - | CONDUIT | 1 - CONDUIT
CONDUITS | 1 1/2'' | EMT | [8 empty] | 1 1/2'' |  | EMT | 1 1/2'' EMT | [18 empty] | INPUT | EMT
[23 empty] | OVER CURRENT MODULE | [9 empty] | 1. GENERAL | 0 |  | CONDUIT SIZING MODULE
|  |  |  | WIRE SIZE MODULE (4" MAX CONDUIT) | [12 empty] | HIGH VOLTAGE |  | 240 | [13 empty] | 2. RIGID | 0
|  | HI | NEUTRAL | CU/AL? | AL |  |  |  |  | WIRES | [6 empty] | LOW VOLTAGE |  | 120 |  |  |  | FUSE SIZING AMPS | 100 | 0 | [7 empty] | 3. EMT | 3 |  | CONDUIT TYPE | 3
|  | LEG | AMPS | WIRE TEMP | 75 |  | L2 AMPS |  | 0 | 1 | 0 | [5 empty] | PHASE |  | 3Y |  |  |  | # OF PHASE WIRES | 1 | [8 empty] | 4. IMC | 0 |  | WIRE AREA SQ IN | 0.7155
DESIGN AMPS | 84 |  |  | DESIGN AMPS (NDA) | 100 |  | NEUTRAL AMPS |  | 46 | 1 | 46 | [21 empty] | 5. PVC-40 | 0 |  | PERCENT FILL | 0.4
MIN AMPS | 100 |  | 46 | LOOKUP AMPS | 100 |  | 33% OF PHASE |  | 33.3 | 1 | 33.3 | [21 empty] | 6. RIGID/PVC | 0
|  | 0 |  | NET Y/N | Y | 4 | MAX |  | 46 |  | 46 | [11 empty] | LOOKUP | FUSE/BKR | [8 empty] | 7. FLEX | 0 |  | LOOKUP | 40% | CONDUIT | EMT | CONDUIT |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
CONNECTED LOAD |  |  |  | HAR Y/N | N | 0 | [10 empty] | 0 | 0 |  |  |  |  | GROUND | AMP | [8 empty] | 8. LT-FLEX | 0 |  | TABLE | FILL | SIZE | AREA | SIZE |  | SIZE | GENERAL | RIGID | EMT | IMC | PVC-40 | RIGID/PVC | FLEX | LT-FLEX
50% CONNECTED | 0 |  |  | SUBTOTAL |  | 4 | [10 empty] | 100 | [5 empty] | AMPS | RATING | [8 empty] | OUTPUT | 3 |  |  |  |  | SQ IN |  |  |  | AREA | AREA | AREA | AREA | AREA | AREA | AREA | AREA
HARMONIC LOAD | 0 | [21 empty] | 0 | 60 | [11 empty] | 0 | 0.1216 | 0.5 | 0.304 | 0.5 |  |  | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN
| N | [21 empty] | 60 | 70 | [11 empty] | 0.1216 | 0.2132 | 0.75 | 0.533 | 0.75 |  | 0.5 | 0.285 | 0.314 | 0.304 | 0.342 | 0.285 | 0.304 | 0.317 | 0.314
|  |  | ROW | LOOKUP |  |  | ADJUST | SELECTED | WIRE | WIRE | WIRE | 60º C | 75 C | 90º C | ROW | AMPACITY TABLE | [6 empty] | 70 | 80 | [11 empty] | 0.2132 | 0.3456 | 1 | 0.864 | 1 |  | 0.75 | 0.508 | 0.549 | 0.533 | 0.586 | 0.508 | 0.533 | 0.533 | 0.541
|  |  |  | WIRE |  |  | WIRE | WIRE | SIZE | SIZE | PER | AMPS | AMPS | AMPS |  | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | 80 | 90 | [11 empty] | 0.3456 | 0.5984 | 1.25 | 1.496 | 1.25 |  | 1 | 0.817 | 0.888 | 0.864 | 0.959 | 0.832 | 0.864 | 0.817 | 0.872
|  |  |  | AMPS |  |  | AMPS | AMPS | AWG | CODE | PHASE | AL | AL | AL |  | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | 90 | 100 | [11 empty] | 0.5984 | 0.8144 | 1.5 | 2.036 | 1.5 |  | 1.25 | 1.277 | 1.526 | 1.496 | 1.646 | 1.453 | 1.495 | 1.277 | 1.528
|  |  | 101 | 0 |  |  | 50 | 50 | #6 | 5 | 1 | 40 | 50 | 60 | 101 | AWG | CU | CU | CU | AL | AL | AL | 100 | 110 | [11 empty] | 0.8144 | 1.3424 | 2 | 3.356 | 2 |  | 1.5 | 1.857 | 2.071 | 2.036 | 2.223 | 1.986 | 2.036 | 1.857 | 1.979
|  |  | 102 | 50 |  |  | 65 | 65 | #4 | 6 | 1 | 55 | 65 | 75 | 102 | #6 | 55 | 65 | 75 | 40 | 50 | 60 | 110 | 125 | [11 empty] | 1.3424 | 2.3432 | 2.5 | 5.858 | 2.5 |  | 2 | 3.245 | 3.408 | 3.356 | 3.629 | 3.291 | 3.355 | 3.269 | 3.245
|  |  | 103 | 65 |  |  | 75 | 75 | #4 | 6 | 1 | 65 | 75 | 85 | 103 | #4 | 70 | 85 | 95 | 55 | 65 | 75 | 125 | 150 | [11 empty] | 2.3432 | 3.5384 | 3 | 8.846 | 3 |  | 2.5 | 4.695 | 4.866 | 5.858 | 5.135 | 4.695 | 4.788 | 4.909 | 4.879
|  |  | 104 | 75 |  |  | 90 | 90 | #2 | 8 | 1 | 75 | 90 | 100 | 104 | #3 | 85 | 100 | 110 | 65 | 75 | 85 | 150 | 175 | [11 empty] | 3.5384 | 4.618 | 3.5 | 11.545 | 3.5 |  | 3 | 7.069 | 7.499 | 8.846 | 7.922 | 7.268 | 7.393 | 7.069 | 7.475
|  |  | 105 | 90 |  |  | 100 | 100 | #1 | 9 | 1 | 85 | 100 | 115 | 105 | #2 | 95 | 115 | 130 | 75 | 90 | 100 | 175 | 200 | [11 empty] | 4.618 | 5.9012 | 4 | 14.753 | 4 |  | 3.5 | 9.621 | 10.01 | 11.545 | 10.584 | 9.737 | 9.866 | 9.621 | 9.731
|  |  | 106 | 100 |  |  | 120 | 120 | #1/0 | 10 | 1 | 100 | 120 | 135 | 106 | #1 | 110 | 130 | 150 | 85 | 100 | 115 | 200 | 225 | [17 empty] | 4 | 12.554 | 12.833 | 14.753 | 13.631 | 12.554 | 12.73 | 12.566 | 12.692
|  |  | 107 | 120 |  |  | 135 | 135 | #2/0 | 11 | 1 | 115 | 135 | 150 | 107 | #1/0 | 125 | 150 | 170 | 100 | 120 | 135 | 225 | 250 | [11 empty] | CONDUIT SIZE | 1.5 | DIFFERENT SIZE WIRES
|  |  | 108 | 135 |  |  | 155 | 155 | #3/0 | 12 | 1 | 130 | 155 | 175 | 108 | #2/0 | 145 | 175 | 195 | 115 | 135 | 150 | 250 | 300 | [11 empty] | CONDUIT TYPE | EMT
|  |  | 109 | 155 |  |  | 180 | 180 | #4/0 | 13 | 1 | 150 | 180 | 205 | 109 | #3/0 | 165 | 200 | 225 | 130 | 155 | 175 | 300 | 350 | [11 empty] | CONDUIT SIZE | NOT USED | SAME SIZE WIRES
|  |  | 110 | 180 |  |  | 205 | 205 | #250 | 14 | 1 | 170 | 205 | 230 | 110 | #4/0 | 195 | 230 | 260 | 150 | 180 | 205 | 350 | 400 | [11 empty] | CONDUIT SIZE | 1.5 | DIFFERENT SIZE WIRES
|  |  | 111 | 205 |  |  | 230 | 230 | #300 | 15 | 1 | 190 | 230 | 255 | 111 | #250 | 215 | 255 | 290 | 170 | 205 | 230 | 400 | 450 | [11 empty] | # OF WIRES | 5
|  |  | 112 | 230 |  |  | 250 | 250 | #350 | 16 | 1 | 210 | 250 | 280 | 112 | #300 | 240 | 285 | 320 | 190 | 230 | 255 | 450 | 500
| CONDUIT SIZE | 1.5 | 113 | 250 |  |  | 270 | 270 | #400 | 17 | 1 | 225 | 270 | 305 | 113 | #350 | 260 | 310 | 350 | 210 | 250 | 280 | 500 | 600 | [18 empty] | 2: EMT; 3: CONDUIT
|  | 1 1/2'' | 114 | 270 |  |  | 310 | 310 | #500 | 18 | 1 | 260 | 310 | 350 | 114 | #400 | 280 | 335 | 380 | 225 | 270 | 305 | 600 | 700 | [14 empty] | 2-WIRE | 3-WIRE | 4-WIRE |  | 2: AREA; 3: SIZE
|  | 0 | 115 | 310 |  |  | 360 | 360 | #4/0 | 13 | 2 |  |  |  | 115 | #500 | 320 | 380 | 430 | 260 | 310 | 350 | 700 | 800 | [18 empty] | 2: SQ IN
|  | 1 1/2'' | 116 | 360 |  |  | 410 | 410 | #250 | 14 | 2 |  |  |  | 116 | [7 empty] | 800 | 1000 | [11 empty] | 1 | 1 | ERR | 0 | 0 | 0 | 0.63966 | 1: 0.1901; 2: 0.1216; 3: 0.5
|  |  | 117 | 410 |  |  | 460 | 460 | #300 | 15 | 2 |  |  |  | 117 | [7 empty] | 1000 | 1200 | [11 empty] | 2 | 2 | ERR | 0 | 0 | 0 | 1.1215 | 1: 0.1901; 2: 0.2132; 3: 0.75
|  |  | 118 | 460 |  |  | 500 | 500 | #350 | 16 | 2 |  |  |  | 118 | AMPACITY TABLE | [19 empty] | 3 | 3 | ERR | 2 | 0 | 0 | 1.818 | 1: 0.1901; 2: 0.3456; 3: 1
|  |  | 119 | 500 |  |  | 540 | 540 | #400 | 17 | 2 |  |  |  | 119 | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | [13 empty] | 4 | 4 | ERR | 0 | 3 | 0 | 3.1478 | 1: 0.1901; 2: 0.5984; 3: 1.25
|  |  | 120 | 540 |  |  | 620 | 620 | #500 | 18 | 2 |  |  |  | 120 | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | UNDER 800A | 100 | #N/A | [10 empty] | 5 | 5 | ERR | 0 | 0 | 4 | 4.2841 | 1: 0.1901; 2: 0.8144; 3: 1.5
|  |  | 121 | 620 |  |  | 690 | 690 | #300 | 15 | 3 |  |  |  | 121 | AWG | CU | CU | CU | AL | AL | AL | OVER 800A |  | 0 | [10 empty] | 6 | 6 | ERR | 0 | 0 | 0 | 7.0615 | 1: 0.1901; 2: 1.3424; 3: 2
|  |  | 122 | 690 |  |  | 750 | 750 | #350 | 16 | 3 |  |  |  | 122 | #6 | 55 | 65 | 75 | 40 | 50 | 60 | RATING | 100 |  |  | 100 | A-3P |  | 100A-3P | [5 empty] | 7 | 7 | ERR | 0 | 0 | 0 | 12.3261 | 1: 0.1901; 2: 2.3432; 3: 2.5
|  |  | 123 | 750 |  |  | 810 | 810 | #400 | 17 | 3 |  |  |  | 123 | #4 | 70 | 85 | 95 | 55 | 65 | 75 | HI LEG FUSE | [12 empty] | 8 | 8 | ERR | 0 | 0 | 0 | 18.6134 | 1: 0.1901; 2: 3.5384; 3: 3
|  |  | 124 | 810 |  |  | 930 | 930 | #500 | 18 | 3 |  |  |  | 124 | #3 | 85 | 100 | 110 | 65 | 75 | 85 | [13 empty] | 9 | 8 | ERR | 0 | 0 | 0 | 24.2925 | 1: 0.1901; 2: 4.618; 3: 3.5
|  |  | 125 | 930 |  |  | 1000 | 1000 | #350 | 16 | 4 |  |  |  | 125 | #2 | 95 | 115 | 130 | 75 | 90 | 100 | [13 empty] | 10 | 10 | ERR | 0 | 0 | 0 | 31.0426 | 1: 0.1901; 2: 5.9012; 3: 4
|  |  | 126 | 1000 |  |  | 1080 | 1080 | #400 | 17 | 4 |  |  |  | 126 | #1 | 110 | 130 | 150 | 85 | 100 | 115 | WIRE FILL SIZING MODULE
|  |  | 127 | 1080 |  |  | 1240 | 1240 | #500 | 18 | 4 |  |  |  | 127 | #1/0 | 125 | 150 | 170 | 100 | 120 | 135 |  | L1 | [12 empty] | 54 | [5 empty] | 1: L2 RESISTANCE CALCULATION
|  |  | 128 | 1240 |  |  | 1250 | 1250 | #350 | 16 | 5 |  |  |  | 128 | #2/0 | 145 | 175 | 195 | 115 | 135 | 150 | WIRE CODE (NPHC) | 9 | [12 empty] | 4
|  |  | 129 | 1250 |  |  | 1350 | 1350 | #400 | 17 | 5 |  |  |  | 129 | #3/0 | 165 | 200 | 225 | 130 | 155 | 175 | WIRE TYPE (NWTYP) | THW | [18 empty] | 1 | 1 | / | 0.253 | = | 0
|  |  | 130 | 1350 |  |  | 1550 | 1550 | #500 | 18 | 5 |  |  |  | 130 | #4/0 | 195 | 230 | 260 | 150 | 180 | 205 | CU/AL ? | AL | [18 empty] | 2 | 1 | / | 0.253 | = | 0
|  |  | 131 | 1550 |  |  | 1620 | 1620 | #400 | 17 | 6 |  |  |  | 131 | #250 | 215 | 255 | 290 | 170 | 205 | 230 | GND WIRE CODE | 5 | [18 empty] | 3 | 1 | / | 0.253 | = | 0
|  |  | 132 | 1620 |  |  | 1860 | 1860 | #500 | 18 | 6 |  |  |  | 132 | #300 | 240 | 285 | 320 | 190 | 230 | 255 | NEUTRAL Y/N | 0 | 0 | [17 empty] | 4 | 1 | / | 0.253 | = | 0
|  |  |  | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [8 empty] | #350 | 260 | 310 | 350 | 210 | 250 | 280 | #OF WIRE | 4 | 4 | [17 empty] | 5 | 1 | / | 0.253 | = | 0
|  |  |  | SELECTED | WIRE | WIRE | WIRE | [8 empty] | #400 | 280 | 335 | 380 | 225 | 270 | 305 | TOTAL WIRES |  | 4 | [17 empty] | 6 | 1 | / | 0.253 | = | 0
|  |  |  | WIRE | SIZE | SIZE | PER | [8 empty] | #500 | 320 | 380 | 430 | 260 | 310 | 350 | GND WIRE CODE
|  |  |  | AMPS | AWG | CODE | PHASE | [28 empty] | VOLTAGE DROP MODULE | [6 empty] | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0
|  |  | L1-L3 | 100 | #1 | 9 | 1 |  | HI LEG | [13 empty] | WIRE | WIRE | ST |  | WIRE | WIRE | ST | ST | ST | ST | CA | CA | CA |  | 1-PHASE | 3Y
|  |  | L2 | 100 | #1 | 9 | 1 |  | 50 | #6 | 5 |  |  |  |  | TABLE 310.15(B)(6) | [6 empty] | SIZE | SIZE | THW |  | WIRE | WIRE | THW | RHW | THHN | XHHW | THW-CA | THHN-CA | XHHW-CA | CU/AL? | AL | [5 empty] | 1: SINGLE CONDUCTOR; 8: 0.253
|  |  | NETURAL | 50 | #6 | 5 | 1 |  | 50 | #6 | 5 |  |  |  |  | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | AWG | CODE | SIZE |  | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | ONE WAY DISTANCE | 50
|  |  |  | 105 | [11 empty] | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS |  |  | SQ IN |  | AWG | CODE | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | TOTAL LOAD | 84 | 84 |  |  |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.253
[9 empty] | NEUTRAL | [6 empty] | AWG | CU | CU | CU | AL | AL | AL | #10 | 3 | 0.0333 |  | #10 | 3 | 0.0333 | 0.0333 | 0.0211 | 0.0243 | 0.051 | 0.051 | 0.0394 | VOLTAGE | 240
|  |  |  | GROUND SIZE MODULE |  |  |  |  | 50 | #6 | 5 |  |  |  |  | #6 | 55 | 65 | 75 | 40 | 50 | 60 | #8 | 4 | 0.0556 |  | #8 | 4 | 0.0556 | 0.0556 | 0.0366 | 0.0437 | 0.051 | 0.051 | 0.0394 | # OF PHASE WIRES | 1
|  |  |  | GND Y/N? (NGYN) | YES |  |  |  | 50 | #6 | 5 |  |  |  |  | #4 | 100 | 100 | 100 | 55 | 65 | 75 | #6 | 5 | 0.0726 |  | #6 | 5 | 0.0726 | 0.1041 | 0.0507 | 0.059 | 0.066 | 0.0452 | 0.0394 | WIRE CODE | 9 | 9 | 9 | 9
|  |  |  | MAX AMPS (NMA) | 100 | [10 empty] | #3 | 110 | 110 | 110 | 65 | 75 | 85 | #4 | 6 | 0.0973 |  | #4 | 6 | 0.0973 | 0.1333 | 0.0824 | 0.0814 | 0.0881 | 0.073 | 0.053 | WIRE | WIRE | RES | RES | RES |  |  | 1: L1 & L2 RESISTANCE CALCULATION
|  |  |  | CU/AL? (NCUAL2) | AL | [10 empty] | #2 | 125 | 125 | 130 | 100 | 100 | 100 | #3 | 7 | 0.1134 |  | #3 | 7 | 0.1134 | 0.1521 | 0.0973 | 0.0962 |  |  |  | SIZE | SIZE | NEC | NEC | NEC
|  |  |  | GND_TABLE | [11 empty] | #1 | 150 | 150 | 150 | 110 | 110 | 115 | #2 | 8 | 0.1333 |  | #2 | 8 | 0.1333 | 0.175 | 0.1158 | 0.1146 | 0.1194 | 0.1017 | 0.073 | AWG | CODE | AL | CU | AL |  |  | 1 | 1 | / | 0.253 | = | 0
|  |  |  | LOOKUP |  | RATING | SEL | SEL |  | RATING | CU | CU | AL | AL |  | #1/0 | 175 | 175 | 175 | 125 | 125 | 135 | #1 | 9 | 0.1901 |  | #1 | 9 | 0.1901 | 0.266 | 0.1562 | 0.1534 | 0.1698 | 0.1352 | 0.1017 | #6 | 5 | 0.808 | 0.491 | 0.808 |  |  | 2 | 1 | / | 0.253 | = | 0
|  |  |  | GROUND |  | OVER | WIRE | WIRE |  | OVER | WIRE | WIRE | WIRE | WIRE |  | #2/0 | 200 | 200 | 200 | 150 | 150 | 150 | #1/0 | 10 | 0.2223 |  | #1/0 | 10 | 0.2223 | 0.3039 | 0.1855 | 0.1825 | 0.1963 | 0.159 | 0.1352 | #4 | 6 | 0.508 | 0.308 | 0.508 |  |  | 3 | 1 | / | 0.253 | = | 0
|  |  |  | AMPS |  | CURRENT | SIZE | CODE |  | CURRENT | SIZE | CODE | SIZE | CODE |  | #3/0 | 225 | 225 | 225 | 175 | 175 | 175 | #2/0 | 11 | 0.2624 |  | #2/0 | 11 | 0.2624 | 0.3505 | 0.2223 | 0.219 | 0.2332 | 0.1924 | 0.159 | #3 | 7 | 0.403 | 0.245 | 0.403 |  |  | 4 | 1 | / | 0.253 | = | 0
|  |  |  | 0 |  | 60 | #8 | 4 |  | 60 | #10 | 3 | #8 | 4 |  | #4/0 | 250 | 250 | 260 | 200 | 200 | 205 | #3/0 | 12 | 0.3117 |  | #3/0 | 12 | 0.3117 | 0.4072 | 0.2679 | 0.2642 | 0.2733 | 0.229 | 0.1885 | #2 | 8 | 0.319 | 0.194 | 0.319 |  |  | 5 | 1 | / | 0.253 | = | 0
|  |  |  | 60 |  | 100 | #6 | 5 |  | 100 | #8 | 4 | #6 | 5 |  | #250 | 300 | 300 | 300 | 225 | 225 | 230 | #4/0 | 13 | 0.3718 |  | #4/0 | 13 | 0.3718 | 0.4754 | 0.3237 | 0.3197 | 0.3267 | 0.278 | 0.229 | #1 | 9 | 0.253 | 0.154 | 0.253 |  |  | 6 | 1 | / | 0.253 | = | 0
|  |  |  | 100 |  | 200 | #4 | 6 |  | 200 | #6 | 5 | #4 | 6 |  | #300 | 300 | 300 | 320 | 250 | 250 | 255 | #250 | 14 | 0.4596 |  | #250 | 14 | 0.4596 | 0.6291 | 0.397 | 0.3904 | 0.4128 | 0.3525 | 0.2733 | #1/0 | 10 | 0.201 | 0.122 | 0.201
|  |  |  | 200 |  | 300 | #2 | 8 |  | 300 | #4 | 6 | #2 | 8 |  | #350 | 350 | 350 | 350 | 300 | 300 | 300 | #300 | 15 | 0.5281 |  | #300 | 15 | 0.5281 | 0.7088 | 0.4608 | 0.4536 | 0.4717 | 0.4071 | 0.3421 | #2/0 | 11 | 0.159 | 0.0967 | 0.159 |  |  | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0
|  |  |  | 300 |  | 400 | #1 | 9 |  | 400 | #3 | 7 | #1 | 9 |  | #400 | 400 | 400 | 400 | 300 | 300 | 305 | #350 | 16 | 0.5958 |  | #350 | 16 | 0.5958 | 0.787 | 0.5242 | 0.5166 | 0.5281 | 0.4656 | 0.4015 | #3/0 | 12 | 0.126 | 0.0766 | 0.126
|  |  |  | 400 |  | 500 | #1/0 | 10 |  | 500 | #2 | 8 | #1/0 | 10 |  | #500 | 400 | 400 | 430 | 350 | 350 | 350 | #400 | 17 | 0.6619 |  | #400 | 17 | 0.6619 | 0.8626 | 0.5863 | 0.5782 | 0.5876 | 0.5216 | 0.4536 | #4/0 | 13 | 0.1 | 0.0608 | 0.1 |  |  | 1: SINGLE CONDUCTOR; 8: 0.253
|  |  |  | 500 |  | 600 | #2/0 | 11 |  | 600 | #1 | 9 | #2/0 | 11 | [8 empty] | #500 | 18 | 0.7901 |  | #500 | 18 | 0.7901 | 1.0082 | 0.7073 | 0.6984 | 0.6939 | 0.6151 | 0.5026 | #250 | 14 | 0.0847 | 0.0515 | 0.0847
|  |  |  | 600 |  | 800 | #3/0 | 12 |  | 800 | #1/0 | 10 | #3/0 | 12 | [21 empty] | #300 | 15 | 0.0707 | 0.0429 | 0.0707 |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.253
|  |  |  | 800 |  | 1000 | #4/0 | 13 |  | 1000 | #2/0 | 11 | #4/0 | 13 | [8 empty] | L1-L3 WIRE CODE | 9 |  | L1,L3 | L2 | NET | # OF WIRES | [6 empty] | #350 | 16 | 0.0605 | 0.0367 | 0.0605
|  |  |  | 1000 |  | 1200 | #250 | 14 |  | 1200 | #3/0 | 12 | #250 | 14 | [8 empty] | L1-L3 SQ IN | 0.1901 | X | 3 |  |  | 3 | = | 0.5703 | 0.1901 | 0 | 1 | #1 | #400 | 17 | 0.0529 | 0.0321 | 0.0529
|  |  |  | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [15 empty] | L2 WIRE CODE | 9 | [11 empty] | #500 | 18 | 0.0424 | 0.0258 | 0.0424
|  |  |  | GROUND | WIRE | WIRE | WIRE | [15 empty] | L2 SQ IN | 0.1901 | X |  | 1 |  | 0 | = | 0 | 0.1901 | 0 | 3 | #1 | WIRE CODE | 9 | 9 | 9 | 9
|  |  |  | MAX | SIZE | SIZE | PER | [15 empty] | NET WIRE CODE | 5 | [11 empty] | WIRE RES | 0.253 | 0.253 | 0.253 | 0.253
|  |  |  | OVER CURRENT | AWG | CODE | PHASE | [15 empty] | NET SQ IN | 0.0726 | X |  |  | 1 | 1 | = | 0.0726 | 0.0726 | 3 | 4 | #6 | AMPS PER WIRE | 84 | 84 | 0 | 0
|  |  |  | 100 | #6 | 5 | 1 | [15 empty] | GND WIRE CODE | 5
[23 empty] | GND SQ IN | 0.0726 | X |  |  |  | 1 | = | 0.0726 | 0.0726 | 5 | 0 | #6
[23 empty] | TOTAL AREA OF CONDUCTORS | [5 empty] | 5 |  | 0.7155 |  | 8 | 8 | [8 empty] | 3: ( 2 X 50' L X 0.2530 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[29 empty] | AL | (L2) | (N)
[25 empty] | 3 | - | #1 |  | THW | 3-#1 THW AL | [8 empty] | 3D | 3D |  |  | 5: VD %; 6: VD %; 7: VD %; 8: VD %
[25 empty] | 0 | - |  |  | THW | [7 empty] | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3-PHASE Y | L2 | L1 & L3
[25 empty] | 1 | - | #6 |  | THW | 1-#6 THW AL (N) | [5 empty] | 2 | 2 | 2 | 2 | 2 | ( | ( | bar: 1 to 8
[25 empty] | 1 | - | #6 |  | GND | 1-#6 AL GND | [5 empty] | X L | 50 | 50 | 50 | 50 | 2 | 2 | 2 | 2 | 2 | VD | 2.1 | 1.8 | 0.0 | 0.0
[36 empty] | X R | 0.253 | 0.253 | 0.253 | 0.253 | X | X | X | X | X | ÷ | VD ÷ | VD ÷ | VD ÷ | VD ÷
[36 empty] | X I | 84 | 84 | 0 | 0 | L | 50 | 50 | 50 | 50 | VOLTS | 240 | 240 | 240 | 240
[30 empty] | 1- SER CABLE | [5 empty] | = |  |  |  |  | X | ' L X | ' L X | ' L X | ' L X | X | V X | V X | V X | V X
[30 empty] | 4-#1 AL | [5 empty] | ÷ 1000 | 1000 | 1000 | 1000 | 1000 | R | 0.2530 | 0.2530 | 0.2530 | 0.2530 | 100 | 100 | 100 | 100 | 100
[30 empty] | 1-#3 GND | [5 empty] | = |  |  |  |  | X | R X | R X | R X | R X | ) = | ) = | ) = | ) = | ) =
[36 empty] | X 0.866 | 1 | 0.866 | 0.866 | 1 | I | 84.0 | 84.0 | 0.0 | 0.0 | VD | 0.9 | 0.8 | 0.0 | 0.0
[36 empty] | = VD | 2.1 | 1.8 | 0 | 0 | / | A ÷ | A ÷ | A ÷ | A ÷ | % | % VD | % VD | % VD | % VD
[36 empty] | ÷ VOLTS | 240 | 240 | 240 | 240 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | ( VD ÷ VOLTS X 100 ) = VD % | ( 2.1 VD ÷ 240 V X 100 ) = 0.9 % VD | ( 1.8 VD ÷ 240 V X 100 ) = 0.8 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[36 empty] | = VD % | 0.88% | 0.75% | 0% | 0% | X | ) | X | X | ) |  | 0.9 % VD | 0.8 % VD | 0.0 % VD | 0.0 % VD
[25 empty] | 1 | - | 1 1/2'' |  | EMT | 1- SER CABLE | [10 empty] | 0.866 | = | 1: 0.866; 2: 0.866; 3: =
[30 empty] | 4-#1 AL | [10 empty] | ) | 2.1 | 1: ); 2: ); 3: 0.0; 6: 3Y
| FEEDER CONDUIT | [28 empty] | 1-#3 GND | [10 empty] | = | VD | 1: =; 2: =; 3: VD; 6: 0.8 % VD
[41 empty] | VD |  | 1: 1.8; 2: 0.0
| 0 | [25 empty] | - FEEDER PER TABLE 310.15(B)(6) | bar: 1 to 2
[23 empty] | - FEEDER PER TABLE 310.16 - |  |  |  | - FEEDER PER TABLE 310.16 - 75° C
[23 empty] | 75 |  |  |  | - FEEDER PER TABLE 310.16 - 75° C |  |  | - FEEDER PER TABLE 310.16 - 75° C | [11 empty] | 2.1 VD | 1: 1.8 VD; 2: 0.0 VD; 3: 0.0 VD
[23 empty] | ° C | [18 empty] | ( 2 X 50' L X 0.2530 R X 84.0 A ÷ 1,000 ) = 2.1 VD | 1: ( 2 X 50' L X 0.2530 R X 84.0 A ÷ 1,000 X 0.866 ) = 1.8 VD; 2: ( 2 X 50' L X 0.2530 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD; 3: ( 2 X 50' L X 0.2530 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[23 empty] | - FEEDER PER TABLE 310.16 - 75° C | [9 empty] | WIRE | WIRE
[33 empty] | SIZE | WIRE
[33 empty] | CODE | SIZE
AWG
[33 empty] | 3 | #10
[33 empty] | 4 | #8
[33 empty] | 5 | #6 | [5 empty] | VOLTAGE DROP
[33 empty] | 6 | #4 | [5 empty] | Single Phase | ( 2 X 50' L X 0.2530 R X 84.0 A ÷ 1,000 ) = 2.1 VD |  | 2: Voltage Drop %; 3: ( 2.1 VD ÷ 240 V X 100 ) = 0.9 % VD
[33 empty] | 7 | #3 | [5 empty] | Three Phase | ( 2 X 50' L X 0.2530 R X 84.0 A ÷ 1,000 X 0.866 ) = 1.8 VD |  | 2: Voltage Drop %; 3: ( 1.8 VD ÷ 240 V X 100 ) = 0.8 % VD
[33 empty] | 8 | #2 | [5 empty] | Voltage Drop L1 & L3 | ( 2 X 50' L X 0.2530 R X 0.0 A ÷ 1,000 ) = 0.0 VD |  | 2: Voltage Drop % L1 & L3; 3: ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[33 empty] | 9 | #1 | [5 empty] | Voltage Drop L2 ( Hi-Leg ) | ( 2 X 50' L X 0.2530 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD |  | 2: Voltage Drop % L2 ( Hi-Leg ); 3: ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[33 empty] | 10 | #1/0
[33 empty] | 11 | #2/0
[33 empty] | 12 | #3/0
[33 empty] | 13 | #4/0
[33 empty] | 14 | #250
[33 empty] | 15 | #300
[33 empty] | 16 | #350
[33 empty] | 17 | #400
[33 empty] | 18 | #500

## Short (hidden)
NO TRANSFORMER 3-PHASE Y
|  | AFC at Starting Point |  |  | (( | 28875 | AFC x | 1 | UA ) + | 0 | MC ) = | 28875 | AFC
[5 empty] | (( | 28,875 | AFC X | 1.00 | UA ) + | 0 | MC ) = | 28,875 | AFC |  |  |  | (( 28,875 AFC X 1.00 UA ) + 0 MC ) = 28,875 AFC
28,875 AFC
Start > | < 28,875 AFC |  |  |  | < | 28,875 | AFC
[14 empty] | 0.75 | 3/4"
| < ' ' LENGTH |  |  |  | < |  | ' | LENGTH | [5 empty] | 1 | 1" | [8 empty] | SER
| - | [5 empty] | - | [6 empty] | 1.25 | 1 1/4"
| - | [5 empty] | - | [6 empty] | 1.5 | 1 1/2" | [7 empty] | GENERAL | 0
[14 empty] | 2 | 2" | [7 empty] | RIGID | 0
[14 empty] | 2.5 | 2 1/2" | [7 empty] | EMT | 1
[14 empty] | 3 | 3" | [7 empty] | IMC | 0
[14 empty] | 3.5 | 3 1/2" | [7 empty] | PVC-40 | 0
End > | < 8,980 AFC |  |  |  | < | 8,980 | AFC | [6 empty] | 4 | 4" | [7 empty] | RIGID/PVC | 0
[23 empty] | FLEX | 0
[23 empty] | LT-FLEX | 0
| Step 4 - Conductor Factor CF - Formula | [21 empty] | STELL=1 PLASTIC=2 | 5
| Three Phase | [21 empty] | CU=1 AL=2 | 1
Conductor Factor CF - Formula | ( | 1.732 | x | 50 | L x | 28875 | AFC ) ÷ ( | 4699 | C x | 1 | N x | 240 | V ) = | 2.217 |  | CF | Print
| ( | 1.732 | X | 50 | L X | 28,875 | AFC ) ÷ ( | 4,699 | C X | 1 | N X | 240 | V ) = | 2.217 |  | CF | ( 1.732 X 50 L X 28,875 AFC ) ÷ ( 4,699 C X 1 N X 240 V ) = 2.217 CF | [5 empty] | TOTAL | 6
Step 5 - Conductor Multiplier CM - Formula
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 2.217 | CF ) = | 0.311 | CM | [7 empty] | Print
| ( | 1 | ) ÷ ( | 1 | + | 2.217 | CF ) = | 0.311 | CM | [7 empty] | ( 1 ) ÷ ( 1 + 2.217 CF ) = 0.311 CM
6
Step 6 - Conductor Let-Through Current CLC - Formula
Conductor Let-Through Current CLC - Formula | ( | 28875 | AFC X | 0.311 | CM ) = | 8980.125 | CLC | [9 empty] | Print | [5 empty] | 6 |  | 1 | 2 | 3 | 4 | 5 | 6
| ( | 28,875 | AFC X | 0.311 | CM ) = | 8,980 | CLC |  |  | 8,980 CLC | [6 empty] | ( 28,875 AFC X 0.311 CM ) = 8,980 CLC | [5 empty] | SER-ROMEX | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit | SER-ROMEX | SER-ROMEX
[23 empty] | CABLE |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | CABLE | CABLE
|  |  | ( 28,875 AFC X 0.311 CM ) = 8,980 CLC | [15 empty] | C7 | #1 | 9 |  | AL |  | Cables CU | Cables CU | Cables AL | Cables AL | CU | AL
[18 empty] | #1 |  |  |  | 1 | 237 | #14 | 389 | 389 | 237 | 237 | 389 | 237
[18 empty] | #1 |  |  |  | 2 | 376 | #12 | 617 | 617 | 376 | 376 | 617 | 376
[22 empty] | 3 | 599 | #10 | 981 | 982 | 599 | 599 | 982 | 599
[22 empty] | 4 | 952 | #8 | 1557 | 1559 | 951 | 952 | 1560 | 952
[22 empty] | 5 | 1482 | #6 | 2425 | 2430 | 1481 | 1482 | 2433 | 1482
[22 empty] | 6 | 2353 | #4 | 3806 | 3826 | 2346 | 2350 | 3838 | 2353
[22 empty] | 7 | 2966 | #3 | 4774 | 4811 | 2952 | 2961 | 4833 | 2966
[22 empty] | 8 | 3740 | #2 | 5907 | 6044 | 3713 | 3730 | 6087 | 3740
[21 empty] | 9 | 9 | 4699 | #1 | 7293 | 7493 | 4645 | 4678 | 7579 | 4699
[22 empty] | 10 | 5876 | #1/0 | 8925 | 9317 | 5777 | 5838 | 9473 | 5876
[22 empty] | 11 | 7373 | #2/0 | 10755 | 11424 | 7187 | 7301 | 11703 | 7373
[22 empty] | 12 | 9243 | #3/0 | 12844 | 13923 | 8826 | 9110 | 14410 | 9243
[22 empty] | 13 | 11409 | #4/0 | 15082 | 16673 | 10741 | 11174 | 17438 | 11409
[22 empty] | 14 | 13236 | #250 | 16483 | 18594 | 12122 | 12862 | 19779 | 13236
[22 empty] | 15 | 15495 | #300 | 18177 | 20868 | 13910 | 14923 | 22525 | 15495
[22 empty] | 16 | 17635 | #350 | 19704 | 22737 | 15484 | 16813 | 24904 | 17635
[22 empty] | 17 | 19588 | #400 | 20566 | 24297 | 16671 | 18506 | 26916 | 19588
[22 empty] | 18 | 23018 | #500 | 22185 | 26706 | 18756 | 21391 | 30096 | 23018
[22 empty] | 4699 | #1

## S-Sec Cable (hidden)
0
TABLE 310.15(B)(6) | NO | 0
HIGH VOLTAGE | 240 | [11 empty] | TABLE
LOW VOLTAGE | 120 | [5 empty] | SHORT | WIRE | WIRE | GROUND | MAX |  | 310.15 |  |  | 3-COND W/GND SER CABLE AL
PHASE | 3Y | [5 empty] | C VALUE | RES | SIZE | SIZE | AMPS | [15 empty] | TABLE | AMPACITY TABLE
AMPS | 100 | 0 | SER 3C AL | SER CABLE | 3-#1 AL | 1-#3 GND | 4699 | 0.253 | #1 | #3 | 100 | 1-1-1-3 | 0 | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | 310.15(B)(6) | WIRE | 60º C | 75 C | 90º C | TABLE
WIRE TEMP | 75 | 0 | SER 3C CU | SER CABLE | 3-#3 CU | 1-#5 GND | 4833 | 0.245 | #3 | #5 | 100 | 3-3-3-5 | 0 | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | AMPS | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
# OF CONDUCTORS | 4 | 1 | SER 4C AL | SER CABLE | 4-#1 AL | 1-#3 GND | 4699 | 0.253 | #1 | #3 | 100 | 1-1-1-1-3 | 0 | [5 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
CU OR AL | AL | 0 | ROMEX 3C CU | ROMEX | 3-#2 CU | 1-#8 GND | 4833 | 0.194 | #2 | #8 | 115 | 2-2-2-2 |  |  |  |  | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
FEEDER TYPE | SER | 0 | MC 3C AL | MC CABLE | 3-#1 AL | 1-#4 GND | 4686 | 0.253 | #1 | #4 | 100 | 1-1-1-4 | 0 |  |  |  | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
|  | 0 | MC 4C AL | MC CABLE | 4-#1 AL | 1-#4 GND | 4686 | 0.253 | #1 | #4 | 100 | 1-1-1-1-4 | 0 |  |  |  | 102 | 65 | 2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3740 | 0.319 |  | #2 | 75 | 90 | 100 | 100 | 0 | 0
|  | 0 | MC 3C CU | MC CABLE | 3-#3 CU | 1-#6 GND | 4820 | 0.245 | #3 | #6 | 100 | 3-3-3-6 | 0 |  |  |  | 103 | 90 | 1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 |  | #1 | 85 | 100 | 115 | 110 | 0 | 0
|  | 0 | MC 4C CU | MC CABLE | 4-#3 CU | 1-#6 GND | 4820 | 0.245 | #3 | #6 | 100 | 3-3-3-3-6 | 0 |  |  |  | 104 | 100 | 1/0-1/0-1/0-2 | #1/0 | #2 | 120 | 10 | 104 | 5876 | 0.201 |  | #1/0 | 100 | 120 | 135 | 125 | 0 | 0
[17 empty] | 105 | 120 | 2/0-2/0-2/0-1 | #2/0 | #1 | 135 | 11 | 105 | 7373 | 0.159 |  | #2/0 | 115 | 135 | 150 | 150 | 0 | 0
[17 empty] | 106 | 135 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 155 | 12 | 106 | 9243 | 0.126 |  | #3/0 | 130 | 155 | 175 | 175 | 0 | 0
|  |  | SER 4C AL | SER CABLE | 4-#1 AL | 1-#3 GND | 4699 | 0.253 | #1 | #3 | 100 | 1-1-1-1-3 | 0 |  |  |  | 107 | 155 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 180 | 13 | 107 | 11409 | 0.1 |  | #4/0 | 150 | 180 | 205 | 200 | 0 | 0 |  | 0
[17 empty] | 108 | 180 | EXCEED | EXCEED | EXCEED | 180 | EXCEED | 108 | EXCEED | EXCEED
|  |  | SER 4C AL | SER CABLE | 4-#1 AL | 1-#3 GND | 4699 | 0.253 | #1 | #3 | 100 | 1-1-1-1-3 | 0 | [14 empty] | #1/0 | 100 | 120
[14 empty] | - FEEDER PER TABLE 310.16 - |  |  | 103 |  | 1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 |  | #2/0 | 115 | 135
[14 empty] | - FEEDER PER TABLE 310.15(B)(6) | [13 empty] | #3/0 | 130 | 155
[14 empty] | 75 |  |  |  |  | SER CABLE |  |  |  |  | SER CABLE |  |  |  | #4/0 | 150 | 180
[14 empty] | ° C |  |  |  |  | 3- | #1 | AL |  |  | 3-#1 AL
|  |  | THE DESIGN LOAD OF | 100 | AMPS EXCEEDS THE |  |  |  | THE DESIGN LOAD OF 100 AMPS EXCEEDS THE | [9 empty] | 1- | #3 | GND |  |  | 1-#3 GND
|  |  | MAXIMUM CABLE RATING OF | 100 | AMPS |  |  |  | MAXIMUM CABLE RATING OF 100 AMPS |  |  |  |  | - FEEDER PER TABLE 310.16 - 75° C
3-COND W/GND SER CABLE CU
|  |  | 1- | SER CABLE |  |  |  | 1- SER CABLE | [19 empty] | AMPACITY TABLE
|  |  | 4-#1 AL |  |  |  |  | 4-#1 AL | [5 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
|  |  | 1-#3 GND |  |  |  |  | 1-#3 GND |  |  |  | � |  | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | CU | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 65 | 5 | 100 | 2433 | 0.491 |  | #6 | 55 | 65 | 75
[17 empty] | 101 | 65 | 4-4-4-6 | #4 | #6 | 85 | 6 | 101 | 3838 | 0.308 |  | #4 | 70 | 85 | 95 | 100 | 0 | 0 | 0
[17 empty] | 102 | 85 | 3-3-3-5 | #3 | #5 | 100 | 7 | 102 | 4833 | 0.245 |  | #3 | 85 | 100 | 110 | 110 | 0 | 0
[17 empty] | 103 | 100 | 2-2-2-4 | #2 | #4 | 115 | 8 | 103 | 6087 | 0.194 |  | #2 | 95 | 115 | 130 | 125 | 0 | 0
[17 empty] | 104 | 115 | 1-1-1-3 | #1 | #3 | 130 | 9 | 104 | 7579 | 0.154 |  | #1 | 110 | 130 | 150 | 150 | 0 | 0
[17 empty] | 105 | 130 | 1/0-1/0-1/0-2 | #1/0 | #2 | 150 | 10 | 105 | 9473 | 0.122 |  | #1/0 | 125 | 150 | 170 | 175 | 0 | 0 | 0
[17 empty] | 106 | 150 | 2/0-2/0-2/0-1 | #2/0 | #1 | 175 | 11 | 106 | 11703 | 0.0967 |  | #2/0 | 145 | 175 | 195 | 200 | 0 | 0 | 0
[17 empty] | 107 | 175 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 200 | 12 | 107 | 14410 | 0.0766 |  | #3/0 | 165 | 200 | 225 | 225 | 0 | 0
[17 empty] | 108 | 200 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 230 | 13 | 108 | 17483 | 0.0608 |  | #4/0 | 195 | 230 | 260 | 250 | 0 | 0 |  | 0
[17 empty] | 109 | 230 | EXCEED | EXCEED | EXCEED | 230 | EXCEED | 109 | EXCEED | EXCEED
[17 empty] | 102 |  | 3-3-3-5 | #3 | #5 | 100 | 7 | 102 | 4833 | 0.245
[19 empty] | SER CABLE |  |  |  |  | SER CABLE
[19 empty] | 3- | #3 | CU |  |  | 3-#3 CU
[19 empty] | 1- | #5 | GND |  |  | 1-#5 GND
4-COND W/GND SER CABLE AL
AMPACITY TABLE
[14 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
[17 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
[17 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
[17 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3740 | 0.319 |  | #2 | 75 | 90 | 100 | 100 | 0 | 0
[17 empty] | 103 | 90 | 1-1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 |  | #1 | 85 | 100 | 115 | 110 | 0 | 0
[17 empty] | 104 | 100 | 1/0-1/0-1/0-1/0-2 | #1/0 | #2 | 120 | 10 | 104 | 5876 | 0.201 |  | #1/0 | 100 | 120 | 135 | 125 | 0 | 0
[17 empty] | 105 | 120 | 2/0-2/0-2/0-2/0-1 | #2/0 | #1 | 135 | 11 | 105 | 7373 | 0.159 |  | #2/0 | 115 | 135 | 150 | 150 | 0 | 0
[17 empty] | 106 | 135 | 3/0-3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 155 | 12 | 106 | 9243 | 0.126 |  | #3/0 | 130 | 155 | 175 | 175 | 0 | 0
[17 empty] | 107 | 155 | 4/0-4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 180 | 13 | 107 | 11409 | 0.1 |  | #4/0 | 150 | 180 | 205 | 200 | 0 | 0
[17 empty] | 108 | 180 | 250-250-250-250-3/0 | #250 | #3/0 | 205 | 14 | 108 | 13236 | 0.0847 |  | #250 | 170 | 205 | 230 | 225 | 0 | 0
[17 empty] | 109 | 205 | 300-300-300-300-4/0 | #300 | #4/0 | 230 | 15 | 109 | 15495 | 0.0707 |  | #300 | 190 | 230 | 255 | 250 | 0 | 0 |  | 0
[17 empty] | 110 | 230 | EXCEED | EXCEED | EXCEED | 230 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 103 |  | 1-1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253
[19 empty] | SER CABLE |  |  |  |  | SER CABLE
[19 empty] | 4- | #1 | AL |  |  | 4-#1 AL
[19 empty] | 1- | #3 | GND |  |  | 1-#3 GND
3-COND W/GND ROMEX CABLE CU
AMPACITY TABLE
[14 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS
[19 empty] | AWG |  |  | AL | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 6-6-6-6 | #6 | #10 | 65 | 5 | 100 | 2433 | 0.491 |  | #6 | 55 | 65 | 75
[17 empty] | 101 | 65 | 4-4-4-4 | #4 | #8 | 85 | 6 | 101 | 3838 | 0.308 |  | #4 | 70 | 85 | 95
[17 empty] | 102 | 85 | 2-2-2-2 | #2 | #8 | 115 | 7 | 102 | 4833 | 0.194 |  | #2 | 95 | 115 | 130
[17 empty] | 103 | 115 | EXCEED | EXCEED | EXCEED | 115 | EXCEED | 103 | EXCEED | EXCEED
[28 empty] | #2 | 95 | 115 | 130
[17 empty] | 102 |  | 2-2-2-2 | #2 | #8 | 115 | 7 | 102 | 4833 | 0.194
[19 empty] | ROMEX |  |  |  |  | ROMEX
[19 empty] | 3- | #2 | CU |  |  | 3-#2 CU
[19 empty] | 1- | #8 | GND |  |  | 1-#8 GND
3-COND W/GND MC CABLE AL
AMPACITY TABLE
[14 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
[17 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
[17 empty] | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
[17 empty] | 102 | 65 | 2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3734 | 0.319 |  | #2 | 75 | 90 | 100 | 100 | 0 | 0
[17 empty] | 103 | 90 | 1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253 |  | #1 | 85 | 100 | 115 | 110 | 0 | 0
[17 empty] | 104 | 100 | 1/0-1/0-1/0-4 | #1/0 | #4 | 120 | 10 | 104 | 5852 | 0.201 |  | #1/0 | 100 | 120 | 135 | 125 | 0 | 0
[17 empty] | 105 | 120 | 2/0-2/0-2/0-4 | #2/0 | #4 | 135 | 11 | 105 | 7327 | 0.159 |  | #2/0 | 115 | 135 | 150 | 150 | 0 | 0
[17 empty] | 106 | 135 | 3/0-3/0-3/0-4 | #3/0 | #4 | 155 | 12 | 106 | 9077 | 0.126 |  | #3/0 | 130 | 155 | 175 | 175 | 0 | 0
[17 empty] | 107 | 155 | 4/0-4/0-4/0-2 | #4/0 | #2 | 180 | 13 | 107 | 11185 | 0.1 |  | #4/0 | 150 | 180 | 205 | 200 | 0 | 0
[17 empty] | 108 | 180 | 250-250-250-2 | #250 | #2 | 205 | 14 | 108 | 12797 | 0.0847 |  | #250 | 170 | 205 | 230 | 225 | 0 | 0
[17 empty] | 109 | 205 | 350-350-350-1 | #300 | #1 | 250 | 16 | 109 | 16795 | 0.0605 |  | #350 | 210 | 250 | 280 | 250 | 0 | 0 |  | 0
[17 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 103 |  | 1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 3- | #1 | AL |  |  | 3-#1 AL
[19 empty] | 1- | #4 | GND |  |  | 1-#4 GND
4-COND W/GND MC CABLE AL
AMPACITY TABLE
[14 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | AL |  | AWG | AL | AL | AL
[17 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 |  | #6 | 40 | 50 | 60
[17 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 |  | #4 | 55 | 65 | 75
[17 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3734 | 0.319 |  | #2 | 75 | 90 | 100 | 100 | 0 | 0
[17 empty] | 103 | 90 | 1-1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253 |  | #1 | 85 | 100 | 115 | 110 | 0 | 0
[17 empty] | 104 | 100 | 1/0-1/0-1/0-1/0-4 | #1/0 | #4 | 120 | 10 | 104 | 5852 | 0.201 |  | #1/0 | 100 | 120 | 135 | 125 | 0 | 0
[17 empty] | 105 | 120 | 2/0-2/0-2/0-2/0-4 | #2/0 | #4 | 135 | 11 | 105 | 7327 | 0.159 |  | #2/0 | 115 | 135 | 150 | 150 | 0 | 0
[17 empty] | 106 | 135 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 155 | 12 | 106 | 9077 | 0.126 |  | #3/0 | 130 | 155 | 175 | 175 | 0 | 0
[17 empty] | 107 | 155 | 4/0-4/0-4/0-4/0-2 | #4/0 | #2 | 180 | 13 | 107 | 11185 | 0.1 |  | #4/0 | 150 | 180 | 205 | 200 | 0 | 0
[17 empty] | 108 | 180 | 250-250-250-250-1 | #250 | #1 | 205 | 14 | 108 | 12797 | 0.0847 |  | #250 | 170 | 205 | 230 | 225 | 0 | 0
[17 empty] | 109 | 205 | 350-350-350-350-1/0 | #350 | #1/0 | 250 | 16 | 109 | 16795 | 0.0605 |  | #350 | 210 | 250 | 280 | 250 | 0 | 0 |  | 0
[17 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 103 |  | 1-1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 4- | #1 | AL |  |  | 4-#1 AL
[19 empty] | 1- | #4 | GND |  |  | 1-#4 GND
3-COND W/GND MC CABLE CU
AMPACITY TABLE
[14 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308 |  | #4 | 70 | 85 | 95 | 100 | 0 | 0 | 0
[17 empty] | 101 | 85 | 3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245 |  | #3 | 85 | 100 | 110 | 110 | 0 | 0
[17 empty] | 102 | 100 | 2-2-2-6 | #2 | #6 | 115 | 8 | 102 | 5989 | 0.194 |  | #2 | 95 | 115 | 130 | 125 | 0 | 0
[17 empty] | 103 | 115 | 1-1-1-6 | #1 | #6 | 130 | 9 | 103 | 7454 | 0.154 |  | #1 | 110 | 130 | 150 | 150 | 0 | 0
[17 empty] | 104 | 130 | 1/0-1/0-1/0-6 | #1/0 | #6 | 150 | 10 | 104 | 9210 | 0.122 |  | #1/0 | 125 | 150 | 170 | 175 | 0 | 0 | 0
[17 empty] | 105 | 150 | 2/0-2/0-2/0-6 | #2/0 | #6 | 175 | 11 | 105 | 11245 | 0.0967 |  | #2/0 | 145 | 175 | 195 | 200 | 0 | 0 | 0
[17 empty] | 106 | 175 | 3/0-3/0-3/0-4 | #3/0 | #4 | 200 | 12 | 106 | 13656 | 0.0766 |  | #3/0 | 165 | 200 | 225 | 225 | 0 | 0
[17 empty] | 107 | 200 | 4/0-4/0-4/0-4 | #4/0 | #4 | 230 | 13 | 107 | 16392 | 0.0608 |  | #4/0 | 195 | 230 | 260 | 250 | 0 | 0
[17 empty] | 108 | 230 | 250-250-250-4 | #250 | #4 | 255 | 14 | 108 | 18311 | 0.0515 |  | #250 | 215 | 255 | 290 | 300 | 0 | 0 | 0
[17 empty] | 109 | 255 | 350-350-350-3 | #350 | #3 | 310 | 16 | 109 | 22646 | 0.0367 |  | #350 | 260 | 310 | 350 | 350 | 0 | 0 |  | 0
[17 empty] | 110 | 310 | EXCEED | EXCEED | EXCEED | 310 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 101 |  | 3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 3- | #3 | CU |  |  | 3-#3 CU
[19 empty] | 1- | #6 | GND |  |  | 1-#6 GND
4-COND W/GND MC CABLE CU
AMPACITY TABLE
[14 empty] | AMPS | 100 |  | ROW | LOOKUP | WIRE | WIRE | NEUTRAL | 75 C | WIRE | ROW | SHORT | RES |  | WIRE | 60º C | 75 C | 90º C | TABLE
[14 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC |  | SIZE | AMPS | AMPS | AMPS | 310.15(B)(6)
[19 empty] | AWG |  |  | AL | NUMBER |  |  | CU |  | AWG | CU | CU | CU
[17 empty] | 100 | 0 | 4-4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308 |  | #4 | 70 | 85 | 95 | 100 | 0 | 0 | 0
[17 empty] | 101 | 85 | 3-3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245 |  | #3 | 85 | 100 | 110 | 110 | 0 | 0
[17 empty] | 102 | 100 | 2-2-2-2-6 | #2 | #6 | 115 | 8 | 102 | 5989 | 0.194 |  | #2 | 95 | 115 | 130 | 125 | 0 | 0
[17 empty] | 103 | 115 | 1-1-1-1-6 | #1 | #6 | 130 | 9 | 103 | 7454 | 0.154 |  | #1 | 110 | 130 | 150 | 150 | 0 | 0
[17 empty] | 104 | 130 | 1/0-1/0-1/0-1/0-6 | #1/0 | #6 | 150 | 10 | 104 | 9210 | 0.122 |  | #1/0 | 125 | 150 | 170 | 175 | 0 | 0 | 0
[17 empty] | 105 | 150 | 2/0-2/0-2/0-2/0-6 | #2/0 | #6 | 175 | 11 | 105 | 11245 | 0.0967 |  | #2/0 | 145 | 175 | 195 | 200 | 0 | 0 | 0
[17 empty] | 106 | 175 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 200 | 12 | 106 | 13656 | 0.0766 |  | #3/0 | 165 | 200 | 225 | 225 | 0 | 0
[17 empty] | 107 | 200 | 4/0-4/0-4/0-4/0-4 | #4/0 | #4 | 230 | 13 | 107 | 16392 | 0.0608 |  | #4/0 | 195 | 230 | 260 | 250 | 0 | 0
[17 empty] | 108 | 230 | 250-250-250-250-4 | #250 | #4 | 255 | 14 | 108 | 18311 | 0.0515 |  | #250 | 215 | 255 | 290 | 300 | 0 | 0 | 0
[17 empty] | 109 | 255 | 350-350-350-350-3 | #350 | #3 | 310 | 16 | 109 | 22646 | 0.0367 |  | #350 | 260 | 310 | 350 | 350 | 0 | 0 |  | 0
[17 empty] | 110 | 310 | EXCEED | EXCEED | EXCEED | 310 | EXCEED | 110 | EXCEED | EXCEED
[17 empty] | 101 |  | 3-3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245
[19 empty] | MC CABLE |  |  |  |  | MC CABLE
[19 empty] | 4- | #3 | CU |  |  | 4-#3 CU
[19 empty] | 1- | #6 | GND |  |  | 1-#6 GND

## Export (hidden)
PANEL | PANEL | BREAKER | FAULT | LENGTH | CONDUIT | WIRE 1 | WIRE 2 | WIRE 3 | WIRE 4 | VD % | SQUARE | APPLIANCE | LAUNDRY | NUMBER | RANGE | NUMBER | DRYER | WATER | WATER | HEAT | HEAT | HEAT | HEAT | HEAT | HEAT | MISC | APP COUNT | APP KVA | APP COUNT | APP KVA
NAME | PHASE | SIZE | CURRENT |  | CABLE | [5 empty] | FOOTAGE | CIRCUITS | CIRCUITS | OF | KVA | OF | KVA | HEATER | HEATER | 1 | 2 | 3 | 4 | 5 | 6 | LOADS | YES | YES | NO | NO
[14 empty] | RANGES |  | DRYERS |  | NUMBER | KVA
DP | 3Y | 100A-3P | 8980.125 | 50' | 1- SER CABLE | 4-#1 AL | 1-#3 GND |  |  | 0.8 % VD | 1500 | 2 | 1 | 1 | 12 | 1 | 5 | 1 | 2.5 | 0 | 0 | 0 | 0 | 0 | 9 | 1200 | 0 | 0 | 0 | 0
DP |  |  | 9 | [6 empty] | 0.8 % VD
|  |  | K | [24 empty] | 0
9 K

## Update Check (hidden)
HIGH | HIGH | LOW | LOW | PHASE | PHASE | FAULT | FAULT | FAULT | FAULT | VD | VD
VOLTS | VOLTS | VOLTS | VOLTS | IN FORM | BACK TO | CURRENT | CURRENT | YES/NO | YES/NO | YES/NO | YES/NO
IN FORM | BACK TO | IN FORM | BACK TO | MAIN | MAIN | IN FORM | BACK TO | IN FORM | BACK TO | IN FORM | BACK TO
MAIN | MAIN | MAIN | MAIN | PANEL | PANEL | MAIN | MAIN | MAIN | MAIN | MAIN | MAIN
PANEL | PANEL | PANEL | PANEL |  |  | PANEL | PANEL | PANEL | PANEL | PANEL | PANEL
240 | 240 | 120 | 120 | 3Y | 3Y | 28875 | 28875 | YRS | YES | YES | YES