## Input
| Residential 1-Line Software 2026 - Version 26.0A - Copyright Durand & Associates | [5 empty] | ERROR |  |  |  | HOUSE PANEL UPDATE |  |  |  |  | MAIN TO HOUSE ERROR |  | 0
Project Name & Address |  | DEMO VERSION |  | Number of Dwelling Units |  |  |  |  | 3 | [6 empty] | MAIN TO DWELLING ERROR |  | 0
[9 empty] | 1 |  | PHASE | 3Y | 1 | 0
| PROJECT NAME | SAMPLE PROJECT |  |  | # OFUNITS | 3 |  |  | 4 |  | HI VOLT | 208 | 208 | 0
| ADDRESS | 123 MAIN ST | [8 empty] | LOW VOLT | 120 | 120 | 0 | [8 empty] | 0
| CITY/STATE/ZIP | SOMEWHERE, CA 95620 | [8 empty] | VD YES/NO |  |  | 0
|  |  |  | Dwelling Unit Lables | [6 empty] | CODE YEAR | 2008 | 2008 | 0 |  | ERRORS | [5 empty] | IN USE | UPDATE | ERROR |  |  | WIRE | WIRE | SYSTEM | AUTO | #500 | 15 | #4 | 1
[14 empty] | 0 | [8 empty] | CHECK |  |  |  | SIZE | SIZE | GROUND | MANUAL |  |  |  | 2
Phase & Voltage |  |  |  |  | DP1 | DP | [12 empty] | DP | 1 | DP1 | 1 | 0 | 0 |  |  | AWG | CODE |  | BUSWAY |  |  |  | 3
| CODE YEAR | 2014 |  |  | DP2 | DP | [12 empty] | DP | 2 | DP2 | 1 | 0 | 0 |  | 1 | #6 | 5 | #8
| PHASE | 3Y |  |  | DP3 | DP | 0 | 0 | [5 empty] | YES |  |  |  |  | DP | 3 | DP3 | 1 | 0 | 0 |  | 2 | #4 | 6 | #8
| HIGH VOLTAGE | 208 |  |  | DP4 | DP | 0 | 0 | [10 empty] | DP | 4 | DP4 | 0 | 0 | 0 |  | 3 | #3 | 6 | #8
| LOW VOLTAGE | 120 |  |  | DP5 | DP | 0 | [11 empty] | DP | 5 | DP5 | 0 | 0 | 0 |  | 4 | #2 | 8 | #8 |  |  |  | #4
[5 empty] | DP6 | DP | 0 | [11 empty] | DP | 6 | DP6 | 0 | 0 | 0 |  | 5 | #1 | 9 | #6 |  |  |  | CU
[5 empty] | DP7 | DP | 0 | [11 empty] | DP | 7 | DP7 | 0 | 0 | 0 |  | 6 | #1/0 | 10 | #6 |  |  |  | -
Main Breaker & House Panel |  |  |  |  | DP8 | DP | [12 empty] | DP | 8 | DP8 | 0 | 0 | 0 |  | 7 | #2/0 | 11 | #6 |  |  |  | #4 CU -
[5 empty] | DP9 | DP | [12 empty] | DP | 9 | DP9 | 0 | 0 | 0 |  | 8 | #3/0 | 12 | #4
| MAIN BREAKER | YES |  |  | DP10 | DP | 0 | [11 empty] | DP | 10 | DP10 | 0 | 0 | 0 |  | 9 | #3/0 | 12 | #4
| MINIMUM SERVICE SIZE | 1200 |  |  | DP11 | DP | 0 | 0 | [10 empty] | DP | 11 | DP11 | 0 | 0 | 0 |  | 10 | #4/0 | 12 | #4
| HOUSE PANEL | YES |  |  | DP12 | DP | 0 | 0 | [10 empty] | DP | 12 | DP12 | 0 | 0 | 0 |  | 11 | #250 | 12 | #4
[5 empty] | DP13 | DP | [12 empty] | DP | 13 | DP13 | 0 | 0 | 0 |  | 12 | #300 | 12 | #4
[5 empty] | DP14 | DP | [12 empty] | DP | 14 | DP14 | 0 | 0 | 0 |  | 13 | #350 | 12 | #4
Voltage Drop, Fault Current & Ufer Ground |  |  |  |  | DP15 | DP | [12 empty] | DP | 15 | DP15 | 0 | 0 | 0 |  | 14 | #400 | 12 | #4
[5 empty] | DP16 | DP | [12 empty] | DP | 16 | DP16 | 0 | 0 | 0 |  | 15 | #500 | 12 | #4
| VOLTAGE DROP CALCS | YES |  |  | DP17 | DP | 0 | [11 empty] | DP | 17 | DP17 | 0 | 0 | 0 |  | 16 | #600 | 12 | #4
| FAULT CURRENT CALCS | YES |  |  | DP18 | DP | 0 | [11 empty] | DP | 18 | DP18 | 0 | 0 | 0 |  | 17 | #750 | 12 | #4
[5 empty] | DP19 | DP |  |  | 0 | K | 0 K | [7 empty] | DP | 19 | DP19 | 0 | 0 | 0 |  | 18 | #1000 | 12 | #4
| SHOW UFER GROUND | YES |  |  | DP20 | DP | 0 |  | 50 | ' | 50' | [7 empty] | DP | 20 | DP20 | 0 | 0 | 0
[5 empty] | DP21 | DP | [12 empty] | DP | 21 | DP21 | 0 | 0 | 0
[5 empty] | DP22 | DP | [12 empty] | DP | 22 | DP22 | 0 | 0 | 0
Service Entrance Feeder |  |  |  |  | DP23 | DP | [12 empty] | DP | 23 | DP23 | 0 | 0 | 0
[5 empty] | DP24 | DP | [12 empty] | DP | 24 | DP24 | 0 | 0 | 0
| SERVICE FEEDER SIZING | AUTO |  |  | DP25 | DP | 0 | [11 empty] | DP | 25 | DP25 | 0 | 0 | 0
| FEEDER TYPE | CONDUIT |  |  | DP26 | DP | 0 | 0 | [10 empty] | DP | 26 | DP26 | 0 | 0 | 0
| LENGTH | 50 |  |  | DP27 | DP | 0 |  |  |  | #6 | [7 empty] | DP | 27 | DP27 | 0 | 0 | 0
| FAULT CURRENT AT SERVICE POINT | 30000 | < < CELL PROTECTED IN DEMO |  | DP28 | DP | 0 |  |  |  | #4 | [7 empty] | DP | 28 | DP28 | 0 | 0 | 0
| WIRE CU/AL | AL |  |  | DP29 | DP | 0 |  |  |  | #3 | [7 empty] | DP | 29 | DP29 | 0 | 0 | 0
| WIRE TEMP | 60 |  |  | DP30 | DP | 0 |  |  |  | #2 | [7 empty] | DP | 30 | DP30 | 0 | 0 | 0
| % FACTOR | 0 |  |  |  |  | 0 |  |  |  | #1 | [9 empty] | HOUSE PANEL |  |  | 0 | 0
| GROUND WIRE | NO |  |  |  |  | 0 |  |  |  | #1/0 | [11 empty] | 0
| WIRE TYPE | THHN |  | Feeder Auto Mode |  |  | 0 |  |  |  | #2/0
| CONDUIT TYPE | EMT |  |  |  |  | 0 |  |  |  | #3/0
| OVERHEAD UNDERGROUND | OVERHEAD |  |  |  | 5-2 1/2'' EMT | 0 |  |  |  | #4/0
[6 empty] | 3-#500 THHN AL |  |  |  |  | #250
[6 empty] | 1-#1/0 THHN AL (N) |  |  |  |  | #300
[11 empty] | #350 |  |  |  | 2" EMT |  | 2" EMT
#400
|  | 2" EMT | [8 empty] | #500
#600
#700
#750
[11 empty] | #1000 |  |  |  | #2 CU | - | #2 CU -
#2 CU
|  | 30000 |  |  |  |  | 0 |  | 30 | K | 30 K
Code Check Ranges | [8 empty] | 30 | K | 30 K
| THIS PROGRAM CALCULATES THE MULTIFAMILY SERVICE SIZE PER NEC 220.84 | [5 empty] | 0 |  |  |  | 30 K
| NEC SECTION 220.84(A)(2) REQUIRES THAT EACH DWELLING HAVE ELECTRIC COOKING EQUIPMENT. | [9 empty] | 28776
| YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS AND EACH DWELLING HAS A RANGE | [10 empty] | 28.8 | K | 28.8 K
| THIS MEETS THE REQUIREMENTS OF NEC 220.84(A)(2) EXCEPTION | [10 empty] | 30
Code Check Electric Heating or Air Conditioning
0
THIS PROGRAM CALCULATES THE MULTIFAMILY SERVICE SIZE PER NEC 220.84
NEC SECTION 220.84(A)(3) REQUIRES THAT EACH DWELLING HAVE ELECTRIC HEATING OR AIR CONDITIONING.
YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS, HOWEVER, ONLY 30 OF THE DWELLINGS
HAVE A HEATING OR AIR CONDITIONING LOADS. CHECK EACH DWELLING AND MAKE SURE EACH
DWELLING HAS A HEATING OR AIR CONDITIONING LOAD.
IF ANY OF THE DWELLINGS DO NOT HAVE A HEATING OR AIR CONDITIONING LOAD YOU WILL NEED
TO ENTER A LOAD. THIS WILL MEET THE REQUIREMENTS OF NEC 220.84(A)(3)
0

## Conduit (hidden)
# OF CONDUITS
5 | - | 2 1/2'' |  | EMT | ( | 4 | - | #500 |  |  | 5 | - | CONDUITS | 5 - CONDUITS
CONDUITS | 5 - 2 1/2'' | EMT | [8 empty] | 2 1/2'' |  | EMT | 2 1/2'' EMT | [17 empty] | INPUT | EMT
[22 empty] | OVER CURRENT MODULE | [9 empty] | 1. GENERAL | 0 |  | CONDUIT SIZING MODULE
|  |  |  | WIRE SIZE MODULE (4" MAX CONDUIT) | [27 empty] | 2. RIGID | 0
|  | HI | NEUTRAL | CU/AL? | AL |  |  |  |  | WIRES | [11 empty] | FUSE SIZING AMPS | 1200 | 0 | [7 empty] | 3. EMT | 3 |  | CONDUIT TYPE | 3
|  | LEG | AMPS | WIRE TEMP | 60 |  | L2 AMPS |  | 0 | 5 | 0 | [10 empty] | # OF PHASE WIRES | 5 | [8 empty] | 4. IMC | 0 |  | WIRE AREA SQ IN | 2.3074
DESIGN AMPS | 1113 |  |  | DESIGN AMPS (NDA) | 1200 |  | NEUTRAL AMPS |  | 422.6 | 5 | 84.52 | [20 empty] | 5. PVC-40 | 0 |  | PERCENT FILL | 0.4
MIN AMPS | 1200 |  | 422.6 | LOOKUP AMPS | 1200 |  | 33% OF PHASE |  | 433.4 | 5 | 86.68 | [20 empty] | 6. RIGID/PVC | 0
|  | 0 |  | NET Y/N | Y | 4 | MAX |  | 433.4 |  | 86.68 | [10 empty] | LOOKUP | FUSE/BKR | [8 empty] | 7. FLEX | 0 |  | LOOKUP | 40% | CONDUIT | EMT | CONDUIT |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
CONNECTED LOAD |  |  |  | HAR Y/N | N | 0 | [15 empty] | GROUND | AMP | [8 empty] | 8. LT-FLEX | 0 |  | TABLE | FILL | SIZE | AREA | SIZE |  | SIZE | GENERAL | RIGID | EMT | IMC | PVC-40 | RIGID/PVC | FLEX | LT-FLEX
50% CONNECTED | 0 |  |  | SUBTOTAL |  | 4 | [15 empty] | AMPS | RATING | [8 empty] | OUTPUT | 3 |  |  |  |  | SQ IN |  |  |  | AREA | AREA | AREA | AREA | AREA | AREA | AREA | AREA
HARMONIC LOAD | 0 | [20 empty] | 0 | 60 | [11 empty] | 0 | 0.1216 | 0.5 | 0.304 | 0.5 |  |  | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN
| N | [20 empty] | 60 | 70 | [11 empty] | 0.1216 | 0.2132 | 0.75 | 0.533 | 0.75 |  | 0.5 | 0.285 | 0.314 | 0.304 | 0.342 | 0.285 | 0.304 | 0.317 | 0.314
|  |  |  | LOOKUP |  |  | ADJUST | SELECTED | WIRE | WIRE | WIRE | 60º C | 75 C | 90º C | AMPACITY TABLE | [6 empty] | 70 | 80 | [11 empty] | 0.2132 | 0.3456 | 1 | 0.864 | 1 |  | 0.75 | 0.508 | 0.549 | 0.533 | 0.586 | 0.508 | 0.533 | 0.533 | 0.541
|  |  |  | WIRE |  |  | WIRE | WIRE | SIZE | SIZE | PER | AMPS | AMPS | AMPS | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | 80 | 90 | [11 empty] | 0.3456 | 0.5984 | 1.25 | 1.496 | 1.25 |  | 1 | 0.817 | 0.888 | 0.864 | 0.959 | 0.832 | 0.864 | 0.817 | 0.872
|  |  |  | AMPS |  |  | AMPS | AMPS | AWG | CODE | PHASE | AL | AL | AL | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | 90 | 100 | [11 empty] | 0.5984 | 0.8144 | 1.5 | 2.036 | 1.5 |  | 1.25 | 1.277 | 1.526 | 1.496 | 1.646 | 1.453 | 1.495 | 1.277 | 1.528
|  |  |  | 0 |  |  | 40 | 40 | #6 | 5 | 1 | 40 | 50 | 60 | AWG | CU | CU | CU | AL | AL | AL | 100 | 110 | [11 empty] | 0.8144 | 1.3424 | 2 | 3.356 | 2 |  | 1.5 | 1.857 | 2.071 | 2.036 | 2.223 | 1.986 | 2.036 | 1.857 | 1.979
|  |  |  | 40 |  |  | 55 | 55 | #4 | 6 | 1 | 55 | 65 | 75 | #6 | 55 | 65 | 75 | 40 | 50 | 60 | 110 | 125 | [11 empty] | 1.3424 | 2.3432 | 2.5 | 5.858 | 2.5 |  | 2 | 3.245 | 3.408 | 3.356 | 3.629 | 3.291 | 3.355 | 3.269 | 3.245
|  |  |  | 55 |  |  | 65 | 65 | #4 | 6 | 1 | 65 | 75 | 85 | #4 | 70 | 85 | 95 | 55 | 65 | 75 | 125 | 150 | [11 empty] | 2.3432 | 3.5384 | 3 | 8.846 | 3 |  | 2.5 | 4.695 | 4.866 | 5.858 | 5.135 | 4.695 | 4.788 | 4.909 | 4.879
|  |  |  | 65 |  |  | 75 | 75 | #2 | 8 | 1 | 75 | 90 | 100 | #3 | 85 | 100 | 110 | 65 | 75 | 85 | 150 | 175 | [11 empty] | 3.5384 | 4.618 | 3.5 | 11.545 | 3.5 |  | 3 | 7.069 | 7.499 | 8.846 | 7.922 | 7.268 | 7.393 | 7.069 | 7.475
|  |  |  | 75 |  |  | 85 | 85 | #1 | 9 | 1 | 85 | 100 | 115 | #2 | 95 | 115 | 130 | 75 | 90 | 100 | 175 | 200 | [11 empty] | 4.618 | 5.9012 | 4 | 14.753 | 4 |  | 3.5 | 9.621 | 10.01 | 11.545 | 10.584 | 9.737 | 9.866 | 9.621 | 9.731
|  |  |  | 85 |  |  | 100 | 100 | #1/0 | 10 | 1 | 100 | 120 | 135 | #1 | 110 | 130 | 150 | 85 | 100 | 115 | 200 | 225 | [17 empty] | 4 | 12.554 | 12.833 | 14.753 | 13.631 | 12.554 | 12.73 | 12.566 | 12.692
|  |  |  | 100 |  |  | 115 | 115 | #2/0 | 11 | 1 | 115 | 135 | 150 | #1/0 | 125 | 150 | 170 | 100 | 120 | 135 | 225 | 250 | [11 empty] | CONDUIT SIZE | 2.5 | DIFFERENT SIZE WIRES
|  |  |  | 115 |  |  | 130 | 130 | #3/0 | 12 | 1 | 130 | 155 | 175 | #2/0 | 145 | 175 | 195 | 115 | 135 | 150 | 250 | 300 | [11 empty] | CONDUIT TYPE | EMT
|  |  |  | 130 |  |  | 150 | 150 | #4/0 | 13 | 1 | 150 | 180 | 205 | #3/0 | 165 | 200 | 225 | 130 | 155 | 175 | 300 | 350 | [11 empty] | CONDUIT SIZE | NOT USED | SAME SIZE WIRES
|  |  |  | 150 |  |  | 170 | 170 | #250 | 14 | 1 | 170 | 205 | 230 | #4/0 | 195 | 230 | 260 | 150 | 180 | 205 | 350 | 400 | [11 empty] | CONDUIT SIZE | 2.5 | DIFFERENT SIZE WIRES
|  |  |  | 170 |  |  | 190 | 190 | #300 | 15 | 1 | 190 | 230 | 255 | #250 | 215 | 255 | 290 | 170 | 205 | 230 | 400 | 450 | [11 empty] | # OF WIRES | 4
|  |  |  | 190 |  |  | 210 | 210 | #350 | 16 | 1 | 210 | 250 | 280 | #300 | 240 | 285 | 320 | 190 | 230 | 255 | 450 | 500
| CONDUIT SIZE | 2.5 |  | 210 |  |  | 225 | 225 | #400 | 17 | 1 | 225 | 270 | 305 | #350 | 260 | 310 | 350 | 210 | 250 | 280 | 500 | 600 | [18 empty] | 2: EMT; 3: CONDUIT
|  | 0 |  | 225 |  |  | 260 | 260 | #500 | 18 | 1 | 260 | 310 | 350 | #400 | 280 | 335 | 380 | 225 | 270 | 305 | 600 | 700 | [14 empty] | 2-WIRE | 3-WIRE | 4-WIRE |  | 2: AREA; 3: SIZE
|  | 2 1/2'' |  | 260 |  |  | 300 | 300 | #4/0 | 13 | 2 |  |  |  | #500 | 320 | 380 | 430 | 260 | 310 | 350 | 700 | 800 | [18 empty] | 2: SQ IN
|  | 2 1/2'' |  | 300 |  |  | 340 | 340 | #250 | 14 | 2 | [10 empty] | 800 | 1000 | [11 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0.17192 | 1: 0.7073; 2: 0.1216; 3: 0.5
|  |  |  | 340 |  |  | 380 | 380 | #300 | 15 | 2 | [10 empty] | 1000 | 1200 | [11 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0.30143 | 1: 0.7073; 2: 0.2132; 3: 0.75
|  |  |  | 380 |  |  | 420 | 420 | #350 | 16 | 2 | [23 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0.48862 | 1: 0.7073; 2: 0.3456; 3: 1
|  |  |  | 420 |  |  | 450 | 450 | #400 | 17 | 2 | [23 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0.84603 | 1: 0.7073; 2: 0.5984; 3: 1.25
|  |  |  | 450 |  |  | 520 | 520 | #500 | 18 | 2 | [10 empty] | UNDER 800A | 1200 | #N/A | [10 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 1.1514 | 1: 0.7073; 2: 0.8144; 3: 1.5
|  |  |  | 520 |  |  | 570 | 570 | #300 | 15 | 3 | [10 empty] | OVER 800A |  | 0 | [10 empty] | 6 | 0 | 0 | 2 | 0 | 0 | 1.8979 | 1: 0.7073; 2: 1.3424; 3: 2
|  |  |  | 570 |  |  | 630 | 630 | #350 | 16 | 3 | [10 empty] | RATING | 1200 |  |  | 1,200 | A-3P |  | 1,200A-3P | [5 empty] | 7 | 0 | 0 | 0 | 3 | 0 | 3.3129 | 1: 0.7073; 2: 2.3432; 3: 2.5
|  |  |  | 630 |  |  | 675 | 675 | #400 | 17 | 3 | [10 empty] | HI LEG FUSE | [12 empty] | 8 | 8 | 4 | 0 | 0 | 4 | 5.0027 | 1: 0.7073; 2: 3.5384; 3: 3
|  |  |  | 675 |  |  | 780 | 780 | #500 | 18 | 3 | [23 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 6.5291 | 1: 0.7073; 2: 4.618; 3: 3.5
|  |  |  | 780 |  |  | 840 | 840 | #350 | 16 | 4 | [23 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 8.3433 | 1: 0.7073; 2: 5.9012; 3: 4
|  |  |  | 840 |  |  | 900 | 900 | #400 | 17 | 4 | [10 empty] | WIRE FILL SIZING MODULE
|  |  |  | 900 |  |  | 1040 | 1040 | #500 | 18 | 4 | [11 empty] | L1 | [12 empty] | 8 | [5 empty] | 1: L2 RESISTANCE CALCULATION
|  |  |  | 1040 |  |  | 1050 | 1050 | #350 | 16 | 5 | [10 empty] | WIRE CODE (NPHC) | 18 | [12 empty] | 3
|  |  |  | 1050 |  |  | 1125 | 1125 | #400 | 17 | 5 | [10 empty] | WIRE TYPE (NWTYP) | THHN | [18 empty] | 1 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | 1125 |  |  | 1300 | 1300 | #500 | 18 | 5 | [10 empty] | CU/AL ? | AL | [18 empty] | 2 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | 1300 |  |  | 1350 | 1350 | #400 | 17 | 6 | [10 empty] | GND WIRE CODE | 14 | [18 empty] | 3 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | 1350 |  |  | 1560 | 1560 | #500 | 18 | 6 | [10 empty] | NEUTRAL Y/N | Y | 0 | [17 empty] | 4 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [14 empty] | #OF WIRE | 4 | 4 | [17 empty] | 5 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | SELECTED | WIRE | WIRE | WIRE | [14 empty] | TOTAL WIRES |  | 4 | [17 empty] | 6 | 1 | / | 0.0424 | = | 0
|  |  |  | WIRE | SIZE | SIZE | PER | [14 empty] | GND WIRE CODE
|  |  |  | AMPS | AWG | CODE | PHASE | [27 empty] | VOLTAGE DROP MODULE | [6 empty] | PARALLEL CONDUCTORS |  |  | 1 | / | 117.9245 | = | 0.00848
|  |  | L1-L3 | 1300 | #500 | 18 | 5 |  | HI LEG | [12 empty] | WIRE | WIRE | ST |  | WIRE | WIRE | ST | ST | ST | ST | CA | CA | CA |  | 1-PHASE | 3Y
|  |  | L2 | 1300 | #500 | 18 | 5 |  | 40 | #6 | 5 | [10 empty] | SIZE | SIZE | THHN |  | WIRE | WIRE | THW | RHW | THHN | XHHW | THW-CA | THHN-CA | XHHW-CA | CU/AL? | AL | [5 empty] | 1: SINGLE CONDUCTOR; 8: 0
|  |  | NETURAL | 500 | #1/0 | 10 | 5 |  | 500 | #1/0 | 10 | [10 empty] | AWG | CODE | SIZE |  | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | ONE WAY DISTANCE | 50
[24 empty] | SQ IN |  | AWG | CODE | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | TOTAL LOAD | 1113 | 1113 |  |  |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.0085
[9 empty] | NEUTRAL | [12 empty] | #10 | 3 | 0.0211 |  | #10 | 3 | 0.0333 | 0.0333 | 0.0211 | 0.0243 | 0.051 | 0.051 | 0.0394 | VOLTAGE | 208
|  |  |  | GROUND SIZE MODULE |  |  |  |  | 100 | #1/0 | 10 | [10 empty] | #8 | 4 | 0.0366 |  | #8 | 4 | 0.0556 | 0.0556 | 0.0366 | 0.0437 | 0.051 | 0.051 | 0.0394 | # OF PHASE WIRES | 5
|  |  |  | GND Y/N? (NGYN) | YES |  |  |  | 500 | #1/0 | 10 | [10 empty] | #6 | 5 | 0.0507 |  | #6 | 5 | 0.0726 | 0.1041 | 0.0507 | 0.059 | 0.066 | 0.0452 | 0.0394 | WIRE CODE | 18 | 18 | 18 | 18
|  |  |  | MAX AMPS (NMA) | 1200 | [16 empty] | #4 | 6 | 0.0824 |  | #4 | 6 | 0.0973 | 0.1333 | 0.0824 | 0.0814 | 0.0881 | 0.073 | 0.053 | WIRE | WIRE | RES | RES | RES |  |  | 1: L1 & L2 RESISTANCE CALCULATION
|  |  |  | CU/AL? (NCUAL2) | AL | [16 empty] | #3 | 7 | 0.0973 |  | #3 | 7 | 0.1134 | 0.1521 | 0.0973 | 0.0962 |  |  |  | SIZE | SIZE | NEC | NEC | NEC
|  |  |  | GND_TABLE | [17 empty] | #2 | 8 | 0.1158 |  | #2 | 8 | 0.1333 | 0.175 | 0.1158 | 0.1146 | 0.1194 | 0.1017 | 0.073 | AWG | CODE | AL | CU | AL |  |  | 1 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | LOOKUP |  | RATING | SEL | SEL |  | RATING | CU | CU | AL | AL | [7 empty] | #1 | 9 | 0.1562 |  | #1 | 9 | 0.1901 | 0.266 | 0.1562 | 0.1534 | 0.1698 | 0.1352 | 0.1017 | #6 | 5 | 0.808 | 0.491 | 0.808 |  |  | 2 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | GROUND |  | OVER | WIRE | WIRE |  | OVER | WIRE | WIRE | WIRE | WIRE | [7 empty] | #1/0 | 10 | 0.1855 |  | #1/0 | 10 | 0.2223 | 0.3039 | 0.1855 | 0.1825 | 0.1963 | 0.159 | 0.1352 | #4 | 6 | 0.508 | 0.308 | 0.508 |  |  | 3 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | AMPS |  | CURRENT | SIZE | CODE |  | CURRENT | SIZE | CODE | SIZE | CODE | [7 empty] | #2/0 | 11 | 0.2223 |  | #2/0 | 11 | 0.2624 | 0.3505 | 0.2223 | 0.219 | 0.2332 | 0.1924 | 0.159 | #3 | 7 | 0.403 | 0.245 | 0.403 |  |  | 4 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | 0 |  | 60 | #8 | 4 |  | 60 | #10 | 3 | #8 | 4 | [7 empty] | #3/0 | 12 | 0.2679 |  | #3/0 | 12 | 0.3117 | 0.4072 | 0.2679 | 0.2642 | 0.2733 | 0.229 | 0.1885 | #2 | 8 | 0.319 | 0.194 | 0.319 |  |  | 5 | 1 | / | 0.0424 | = | 23.5849
|  |  |  | 60 |  | 100 | #6 | 5 |  | 100 | #8 | 4 | #6 | 5 | [7 empty] | #4/0 | 13 | 0.3237 |  | #4/0 | 13 | 0.3718 | 0.4754 | 0.3237 | 0.3197 | 0.3267 | 0.278 | 0.229 | #1 | 9 | 0.253 | 0.154 | 0.253 |  |  | 6 | 1 | / | 0.0424 | = | 0
|  |  |  | 100 |  | 200 | #4 | 6 |  | 200 | #6 | 5 | #4 | 6 | [7 empty] | #250 | 14 | 0.397 |  | #250 | 14 | 0.4596 | 0.6291 | 0.397 | 0.3904 | 0.4128 | 0.3525 | 0.2733 | #1/0 | 10 | 0.201 | 0.122 | 0.201
|  |  |  | 200 |  | 300 | #2 | 8 |  | 300 | #4 | 6 | #2 | 8 | [7 empty] | #300 | 15 | 0.4608 |  | #300 | 15 | 0.5281 | 0.7088 | 0.4608 | 0.4536 | 0.4717 | 0.4071 | 0.3421 | #2/0 | 11 | 0.159 | 0.0967 | 0.159 |  |  | PARALLEL CONDUCTORS |  |  | 1 | / | 117.9245 | = | 0.00848
|  |  |  | 300 |  | 400 | #1 | 9 |  | 400 | #3 | 7 | #1 | 9 | [7 empty] | #350 | 16 | 0.5242 |  | #350 | 16 | 0.5958 | 0.787 | 0.5242 | 0.5166 | 0.5281 | 0.4656 | 0.4015 | #3/0 | 12 | 0.126 | 0.0766 | 0.126
|  |  |  | 400 |  | 500 | #1/0 | 10 |  | 500 | #2 | 8 | #1/0 | 10 | [7 empty] | #400 | 17 | 0.5863 |  | #400 | 17 | 0.6619 | 0.8626 | 0.5863 | 0.5782 | 0.5876 | 0.5216 | 0.4536 | #4/0 | 13 | 0.1 | 0.0608 | 0.1 |  |  | 1: SINGLE CONDUCTOR; 8: 0
|  |  |  | 500 |  | 600 | #2/0 | 11 |  | 600 | #1 | 9 | #2/0 | 11 | [7 empty] | #500 | 18 | 0.7073 |  | #500 | 18 | 0.7901 | 1.0082 | 0.7073 | 0.6984 | 0.6939 | 0.6151 | 0.5026 | #250 | 14 | 0.0847 | 0.0515 | 0.0847
|  |  |  | 600 |  | 800 | #3/0 | 12 |  | 800 | #1/0 | 10 | #3/0 | 12 | [20 empty] | #300 | 15 | 0.0707 | 0.0429 | 0.0707 |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.0085
|  |  |  | 800 |  | 1000 | #4/0 | 13 |  | 1000 | #2/0 | 11 | #4/0 | 13 | [7 empty] | L1-L3 WIRE CODE | 18 |  | L1,L3 | L2 | NET | # OF WIRES | [6 empty] | #350 | 16 | 0.0605 | 0.0367 | 0.0605
|  |  |  | 1000 |  | 1200 | #250 | 14 |  | 1200 | #3/0 | 12 | #250 | 14 | [7 empty] | L1-L3 SQ IN | 0.7073 | X | 3 |  |  | 3 | = | 2.1219 | 0.7073 | 0 | 1 | #500 | #400 | 17 | 0.0529 | 0.0321 | 0.0529
|  |  |  | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [14 empty] | L2 WIRE CODE | 18 | [11 empty] | #500 | 18 | 0.0424 | 0.0258 | 0.0424
|  |  |  | GROUND | WIRE | WIRE | WIRE | [14 empty] | L2 SQ IN | 0.7073 | X |  | 1 |  | 0 | = | 0 | 0.7073 | 0 | 3 | #500 | WIRE CODE | 18 | 18 | 18 | 18
|  |  |  | MAX | SIZE | SIZE | PER | [14 empty] | NET WIRE CODE | 10 | [11 empty] | WIRE RES | 0.0424 | 0.0424 | 0.0424 | 0.0424
|  |  |  | OVER CURRENT | AWG | CODE | PHASE | [14 empty] | NET SQ IN | 0.1855 | X |  |  | 1 | 1 | = | 0.1855 | 0.1855 | 3 | 4 | #1/0 | AMPS PER WIRE | 1113 | 1113 | 0 | 0
|  |  |  | 1200 | #250 | 14 | 5 | [14 empty] | GND WIRE CODE | 14
[22 empty] | GND SQ IN | 0.397 | X |  |  |  | 0 | = | 0 | 0.397 | 5 | 0 | #250
[22 empty] | TOTAL AREA OF CONDUCTORS | [5 empty] | 4 |  | 2.3074 |  | 8 | 8 | [8 empty] | 3: ( 2 X 50' L X 0.0085 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[28 empty] | AL | (L2) | (N)
[24 empty] | 3 | - | #500 |  | THHN | 3-#500 THHN AL | [8 empty] | 3D | 3D |  |  | 5: VD %; 6: VD %; 7: VD %; 8: VD %
[24 empty] | 0 | - |  |  | THHN | [7 empty] | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3-PHASE Y | L2 | L1 & L3
[24 empty] | 1 | - | #1/0 |  | THHN | 1-#1/0 THHN AL (N) | [5 empty] | 2 | 2 | 2 | 2 | 2 | ( | ( | bar: 1 to 8
[24 empty] | 0 | - |  |  | GND | [6 empty] | X L | 50 | 50 | 50 | 50 | 2 | 2 | 2 | 2 | 2 | VD | 0.9 | 0.8 | 0.0 | 0.0
[35 empty] | X R | 0.0085 | 0.0085 | 0.0085 | 0.0085 | X | X | X | X | X | ÷ | VD ÷ | VD ÷ | VD ÷ | VD ÷
[35 empty] | X I | 1113 | 1113 | 0 | 0 | L | 50 | 50 | 50 | 50 | VOLTS | 208 | 208 | 208 | 208
[29 empty] | 3-#500 THHN AL | [5 empty] | = |  |  |  |  | X | ' L X | ' L X | ' L X | ' L X | X | V X | V X | V X | V X
[29 empty] | 1-#1/0 THHN AL (N) | [5 empty] | ÷ 1000 | 1000 | 1000 | 1000 | 1000 | R | 0.0085 | 0.0085 | 0.0085 | 0.0085 | 100 | 100 | 100 | 100 | 100
[35 empty] | = |  |  |  |  | X | R X | R X | R X | R X | ) = | ) = | ) = | ) = | ) =
[35 empty] | X 0.866 | 1 | 0.866 | 0.866 | 1 | I | 1,113.0 | 1,113.0 | 0.0 | 0.0 | VD | 0.4 | 0.4 | 0.0 | 0.0
[35 empty] | = VD | 0.9 | 0.8 | 0 | 0 | / | A ÷ | A ÷ | A ÷ | A ÷ | % | % VD | % VD | % VD | % VD
[35 empty] | ÷ VOLTS | 208 | 208 | 208 | 208 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | ( VD ÷ VOLTS X 100 ) = VD % | ( 0.9 VD ÷ 208 V X 100 ) = 0.4 % VD | ( 0.8 VD ÷ 208 V X 100 ) = 0.4 % VD | ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD
[35 empty] | = VD % | 0.43% | 0.38% | 0% | 0% | X | ) | X | X | ) |  | 0.4 % VD | 0.4 % VD | 0.0 % VD | 0.0 % VD
[24 empty] | 5 | - | 2 1/2'' |  | EMT | 5-2 1/2'' EMT | [10 empty] | 0.866 | = | 1: 0.866; 2: 0.866; 3: =
[29 empty] | 3-#500 THHN AL | [10 empty] | ) | 0.9 | 1: ); 2: ); 3: 0.0; 6: 3Y
| FEEDER CONDUIT | [27 empty] | 1-#1/0 THHN AL (N) | [10 empty] | = | VD | 1: =; 2: =; 3: VD; 6: 0.4 % VD
[40 empty] | VD |  | 1: 0.8; 2: 0.0
0 | bar: 1 to 2
[41 empty] | 0.9 VD | 1: 0.8 VD; 2: 0.0 VD; 3: 0.0 VD
[41 empty] | ( 2 X 50' L X 0.0085 R X 1,113.0 A ÷ 1,000 ) = 0.9 VD | 1: ( 2 X 50' L X 0.0085 R X 1,113.0 A ÷ 1,000 X 0.866 ) = 0.8 VD; 2: ( 2 X 50' L X 0.0085 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD; 3: ( 2 X 50' L X 0.0085 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[32 empty] | WIRE | WIRE
[32 empty] | SIZE | WIRE
[32 empty] | CODE | SIZE
AWG
[32 empty] | 3 | #10
[32 empty] | 4 | #8
[32 empty] | 5 | #6 | [5 empty] | VOLTAGE DROP
[32 empty] | 6 | #4 | [5 empty] | Single Phase | ( 2 X 50' L X 0.0085 R X 1,113.0 A ÷ 1,000 ) = 0.9 VD |  | 2: Voltage Drop %; 3: ( 0.9 VD ÷ 208 V X 100 ) = 0.4 % VD
[32 empty] | 7 | #3 | [5 empty] | Three Phase | ( 2 X 50' L X 0.0085 R X 1,113.0 A ÷ 1,000 X 0.866 ) = 0.8 VD |  | 2: Voltage Drop %; 3: ( 0.8 VD ÷ 208 V X 100 ) = 0.4 % VD
[32 empty] | 8 | #2 | [5 empty] | Voltage Drop L1 & L3 | ( 2 X 50' L X 0.0085 R X 0.0 A ÷ 1,000 ) = 0.0 VD |  | 2: Voltage Drop % L1 & L3; 3: ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD
[32 empty] | 9 | #1 | [5 empty] | Voltage Drop L2 ( Hi-Leg ) | ( 2 X 50' L X 0.0085 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD |  | 2: Voltage Drop % L2 ( Hi-Leg ); 3: ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD
[32 empty] | 10 | #1/0
[32 empty] | 11 | #2/0
[32 empty] | 12 | #3/0
[32 empty] | 13 | #4/0
[32 empty] | 14 | #250
[32 empty] | 15 | #300
[32 empty] | 16 | #350
[32 empty] | 17 | #400
[32 empty] | 18 | #500

## S-Sec Cable (hidden)
[7 empty] | SHORT | WIRE | WIRE | GROUND | MAX |  |  |  | 3-COND W/GND SER CABLE AL
[7 empty] | C VALUE | RES | SIZE | SIZE | AMPS | [14 empty] | AMPACITY TABLE
AMPS | 1200 | 0 | SER 3C AL | SER CABLE | 3-EXCEED AL | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 150 | EXCEED | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
WIRE TEMP | 60 | 0 | SER 3C CU | SER CABLE | 3-EXCEED CU | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 195 | EXCEED | WIRE TEMP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
# OF CONDUCTORS | 4 | 0 | SER 4C AL | SER CABLE | 4-EXCEED AL | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 190 | EXCEED | [5 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
CU OR AL | AL | 0 | ROMEX 3C CU | ROMEX | 3-EXCEED CU | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 95 | EXCEED |  |  |  | 100 | 0 | 6-6-6-6 | #6 | #6 | 40 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
FEEDER TYPE | CONDUIT | 0 | MC 3C AL | MC CABLE | 3-EXCEED AL | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 210 | EXCEED |  |  |  | 101 | 40 | 4-4-4-6 | #4 | #6 | 55 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
|  | 0 | MC 4C AL | MC CABLE | 4-EXCEED AL | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 210 | EXCEED |  |  |  | 102 | 55 | 2-2-2-4 | #2 | #4 | 75 | 8 | 102 | 3740 | 0.319 | #2 | 75 | 90 | 100
|  | 0 | MC 3C CU | MC CABLE | 3-EXCEED CU | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 260 | EXCEED |  |  |  | 103 | 75 | 1-1-1-3 | #1 | #3 | 85 | 9 | 103 | 4699 | 0.253 | #1 | 85 | 100 | 115
|  | 0 | MC 4C CU | MC CABLE | 4-EXCEED CU | 1-EXCEED GND | EXCEED | EXCEED | EXCEED | EXCEED | 260 | EXCEED |  |  |  | 104 | 85 | 1/0-1/0-1/0-2 | #1/0 | #2 | 100 | 10 | 104 | 5876 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 100 | 2/0-2/0-2/0-1 | #2/0 | #1 | 115 | 11 | 105 | 7373 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 115 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 130 | 12 | 106 | 9243 | 0.126 | #3/0 | 130 | 155 | 175
|  |  | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR |  |  |  | 107 | 130 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 150 | 13 | 107 | 11409 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 150 | EXCEED | EXCEED | EXCEED | 150 | EXCEED | 108 | EXCEED | EXCEED
|  |  | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR
[16 empty] | 108 |  | EXCEED | EXCEED | EXCEED | 150 | EXCEED | 108 | EXCEED | EXCEED
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 3- | EXCEED | AL |  |  | 3-EXCEED AL
|  |  | THE DESIGN LOAD OF | 1200 | AMPS EXCEEDS THE |  |  |  | THE DESIGN LOAD OF 1200 AMPS EXCEEDS THE | [8 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
|  |  | MAXIMUM CABLE RATING OF | ERROR | AMPS |  |  |  | MAXIMUM CABLE RATING OF ERROR AMPS
3-COND W/GND SER CABLE CU
|  |  |  | ERROR |  |  |  | ERROR | [17 empty] | AMPACITY TABLE
|  |  | ERROR |  |  |  |  | ERROR |  |  |  |  | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
|  |  | ERROR |  |  |  |  | ERROR |  |  |  |  | WIRE TEMP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | CU | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 55 | 5 | 100 | 2433 | 0.491 | #6 | 55 | 65 | 75
[16 empty] | 101 | 55 | 4-4-4-6 | #4 | #6 | 70 | 6 | 101 | 3838 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 102 | 70 | 3-3-3-5 | #3 | #5 | 85 | 7 | 102 | 4833 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 103 | 85 | 2-2-2-4 | #2 | #4 | 95 | 8 | 103 | 6087 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 104 | 95 | 1-1-1-3 | #1 | #3 | 110 | 9 | 104 | 7579 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 105 | 110 | 1/0-1/0-1/0-2 | #1/0 | #2 | 125 | 10 | 105 | 9473 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 106 | 125 | 2/0-2/0-2/0-1 | #2/0 | #1 | 145 | 11 | 106 | 11703 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 107 | 145 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 165 | 12 | 107 | 14410 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 108 | 165 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 195 | 13 | 108 | 17483 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 109 | 195 | EXCEED | EXCEED | EXCEED | 195 | EXCEED | 109 | EXCEED | EXCEED
[16 empty] | 109 |  | EXCEED | EXCEED | EXCEED | 195 | EXCEED | 109 | EXCEED | EXCEED
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 3- | EXCEED | CU |  |  | 3-EXCEED CU
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
4-COND W/GND SER CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 40 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 40 | 4-4-4-4-6 | #4 | #6 | 55 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 55 | 2-2-2-2-4 | #2 | #4 | 75 | 8 | 102 | 3740 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 75 | 1-1-1-1-3 | #1 | #3 | 85 | 9 | 103 | 4699 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 85 | 1/0-1/0-1/0-1/0-2 | #1/0 | #2 | 100 | 10 | 104 | 5876 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 100 | 2/0-2/0-2/0-2/0-1 | #2/0 | #1 | 115 | 11 | 105 | 7373 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 115 | 3/0-3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 130 | 12 | 106 | 9243 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 130 | 4/0-4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 150 | 13 | 107 | 11409 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 150 | 250-250-250-250-3/0 | #250 | #3/0 | 170 | 14 | 108 | 13236 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 170 | 300-300-300-300-4/0 | #300 | #4/0 | 190 | 15 | 109 | 15495 | 0.0707 | #300 | 190 | 230 | 255
[16 empty] | 110 | 190 | EXCEED | EXCEED | EXCEED | 190 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 110 |  | EXCEED | EXCEED | EXCEED | 190 | EXCEED | 110 | EXCEED | EXCEED
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 4- | EXCEED | AL |  |  | 4-EXCEED AL
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
3-COND W/GND ROMEX CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #10 | 55 | 5 | 100 | 2433 | 0.491 | #6 | 55 | 65 | 75
[16 empty] | 101 | 55 | 4-4-4-4 | #4 | #8 | 70 | 6 | 101 | 3838 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 102 | 70 | 2-2-2-2 | #2 | #8 | 95 | 7 | 102 | 4833 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 95 | EXCEED | EXCEED | EXCEED | 95 | EXCEED | 103 | EXCEED | EXCEED
[16 empty] | 103 |  | EXCEED | EXCEED | EXCEED | 95 | EXCEED | 103 | EXCEED | EXCEED
[18 empty] | ROMEX |  |  |  |  | ROMEX
[18 empty] | 3- | EXCEED | CU |  |  | 3-EXCEED CU
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
3-COND W/GND MC CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 40 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 40 | 4-4-4-6 | #4 | #6 | 55 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 55 | 2-2-2-4 | #2 | #4 | 75 | 8 | 102 | 3734 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 75 | 1-1-1-4 | #1 | #4 | 85 | 9 | 103 | 4686 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 85 | 1/0-1/0-1/0-4 | #1/0 | #4 | 100 | 10 | 104 | 5852 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 100 | 2/0-2/0-2/0-4 | #2/0 | #4 | 115 | 11 | 105 | 7327 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 115 | 3/0-3/0-3/0-4 | #3/0 | #4 | 130 | 12 | 106 | 9077 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 130 | 4/0-4/0-4/0-2 | #4/0 | #2 | 150 | 13 | 107 | 11185 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 150 | 250-250-250-2 | #250 | #2 | 170 | 14 | 108 | 12797 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 170 | 350-350-350-1 | #300 | #1 | 210 | 16 | 109 | 16795 | 0.0605 | #350 | 210 | 250 | 280
[16 empty] | 110 | 210 | EXCEED | EXCEED | EXCEED | 210 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 110 |  | EXCEED | EXCEED | EXCEED | 210 | EXCEED | 110 | EXCEED | EXCEED
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 3- | EXCEED | AL |  |  | 3-EXCEED AL
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
4-COND W/GND MC CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 40 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 40 | 4-4-4-4-6 | #4 | #6 | 55 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 55 | 2-2-2-2-4 | #2 | #4 | 75 | 8 | 102 | 3734 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 75 | 1-1-1-1-4 | #1 | #4 | 85 | 9 | 103 | 4686 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 85 | 1/0-1/0-1/0-1/0-4 | #1/0 | #4 | 100 | 10 | 104 | 5852 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 100 | 2/0-2/0-2/0-2/0-4 | #2/0 | #4 | 115 | 11 | 105 | 7327 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 115 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 130 | 12 | 106 | 9077 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 130 | 4/0-4/0-4/0-4/0-2 | #4/0 | #2 | 150 | 13 | 107 | 11185 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 150 | 250-250-250-250-1 | #250 | #1 | 170 | 14 | 108 | 12797 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 170 | 350-350-350-350-1/0 | #350 | #1/0 | 210 | 16 | 109 | 16795 | 0.0605 | #350 | 210 | 250 | 280
[16 empty] | 110 | 210 | EXCEED | EXCEED | EXCEED | 210 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 110 |  | EXCEED | EXCEED | EXCEED | 210 | EXCEED | 110 | EXCEED | EXCEED
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 4- | EXCEED | AL |  |  | 4-EXCEED AL
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
3-COND W/GND MC CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 4-4-4-8 | #4 | #8 | 70 | 6 | 100 | 3830 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 101 | 70 | 3-3-3-6 | #3 | #6 | 85 | 7 | 101 | 4820 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 102 | 85 | 2-2-2-6 | #2 | #6 | 95 | 8 | 102 | 5989 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 95 | 1-1-1-6 | #1 | #6 | 110 | 9 | 103 | 7454 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 104 | 110 | 1/0-1/0-1/0-6 | #1/0 | #6 | 125 | 10 | 104 | 9210 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 105 | 125 | 2/0-2/0-2/0-6 | #2/0 | #6 | 145 | 11 | 105 | 11245 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 106 | 145 | 3/0-3/0-3/0-4 | #3/0 | #4 | 165 | 12 | 106 | 13656 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 107 | 165 | 4/0-4/0-4/0-4 | #4/0 | #4 | 195 | 13 | 107 | 16392 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 108 | 195 | 250-250-250-4 | #250 | #4 | 215 | 14 | 108 | 18311 | 0.0515 | #250 | 215 | 255 | 290
[16 empty] | 109 | 215 | 350-350-350-3 | #350 | #3 | 260 | 16 | 109 | 22646 | 0.0367 | #350 | 260 | 310 | 350
[16 empty] | 110 | 260 | EXCEED | EXCEED | EXCEED | 260 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 110 |  | EXCEED | EXCEED | EXCEED | 260 | EXCEED | 110 | EXCEED | EXCEED
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 3- | EXCEED | CU |  |  | 3-EXCEED CU
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND
4-COND W/GND MC CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 1200 |  | ROW | LOOKUP | WIRE | WIRE | NEUTRAL | 60º C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 60 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 4-4-4-4-8 | #4 | #8 | 70 | 6 | 100 | 3830 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 101 | 70 | 3-3-3-3-6 | #3 | #6 | 85 | 7 | 101 | 4820 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 102 | 85 | 2-2-2-2-6 | #2 | #6 | 95 | 8 | 102 | 5989 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 95 | 1-1-1-1-6 | #1 | #6 | 110 | 9 | 103 | 7454 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 104 | 110 | 1/0-1/0-1/0-1/0-6 | #1/0 | #6 | 125 | 10 | 104 | 9210 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 105 | 125 | 2/0-2/0-2/0-2/0-6 | #2/0 | #6 | 145 | 11 | 105 | 11245 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 106 | 145 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 165 | 12 | 106 | 13656 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 107 | 165 | 4/0-4/0-4/0-4/0-4 | #4/0 | #4 | 195 | 13 | 107 | 16392 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 108 | 195 | 250-250-250-250-4 | #250 | #4 | 215 | 14 | 108 | 18311 | 0.0515 | #250 | 215 | 255 | 290
[16 empty] | 109 | 215 | 350-350-350-350-3 | #350 | #3 | 260 | 16 | 109 | 22646 | 0.0367 | #350 | 260 | 310 | 350
[16 empty] | 110 | 260 | EXCEED | EXCEED | EXCEED | 260 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 110 |  | EXCEED | EXCEED | EXCEED | 260 | EXCEED | 110 | EXCEED | EXCEED
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 4- | EXCEED | CU |  |  | 4-EXCEED CU
[18 empty] | 1- | EXCEED | GND |  |  | 1-EXCEED GND

## VD (hidden)
|  |  | WIRE | AMPS | PHASE | VD | VOLTS | % VD
ACTIVE |  | LENGTH | RES |  | MULTIPLIER
1 | DP1 | 30 | 0.253 | 98 | 1 | 1.5 | 208 | 0.7 | ( 2 X | 30 | ' L X | 0.2530 | R X | 98 | A ÷ 1,000 X | 1 | ) = | 1.5 | VD | ( 2 X 30' L X 0.2530 R X 98 A ÷ 1,000 X 1 ) = 1.5 VD | ( | 1.5 | VD ÷ | 208 | V X 100 ) = | 0.7 | % VD | ( 1.5 VD ÷ 208 V X 100 ) = 0.7 % VD
1 | DP2 | 30 | 0.253 | 98 | 1 | 1.5 | 208 | 0.7 | ( 2 X | 30 | ' L X | 0.2530 | R X | 98 | A ÷ 1,000 X | 1 | ) = | 1.5 | VD | ( 2 X 30' L X 0.2530 R X 98 A ÷ 1,000 X 1 ) = 1.5 VD | ( | 1.5 | VD ÷ | 208 | V X 100 ) = | 0.7 | % VD | ( 1.5 VD ÷ 208 V X 100 ) = 0.7 % VD
1 | DP3 | 30 | 0.253 | 98 | 1 | 1.5 | 208 | 0.7 | ( 2 X | 30 | ' L X | 0.2530 | R X | 98 | A ÷ 1,000 X | 1 | ) = | 1.5 | VD | ( 2 X 30' L X 0.2530 R X 98 A ÷ 1,000 X 1 ) = 1.5 VD | ( | 1.5 | VD ÷ | 208 | V X 100 ) = | 0.7 | % VD | ( 1.5 VD ÷ 208 V X 100 ) = 0.7 % VD
0 | DP4 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP5 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP6 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP7 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP8 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP9 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP10 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP11 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP12 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP13 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP14 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP15 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP16 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP17 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP18 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP19 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP20 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP21 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP22 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP23 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP24 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP25 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP26 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP27 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP28 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP29 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
0 | DP30 | [7 empty] | ( 2 X |  | ' L X |  | R X |  | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
1 | HP | 10 | 0.491 | 0 | 1 | 0 | 208 | 0 | ( 2 X | 10 | ' L X | 0.4910 | R X | 0 | A ÷ 1,000 X | 1 | ) = | 0.0 | VD | ( 2 X 10' L X 0.4910 R X 0 A ÷ 1,000 X 1 ) = 0.0 VD | ( | 0.0 | VD ÷ | 208 | V X 100 ) = | 0.0 | % VD | ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD
0 | HSP |  | 0.491 | 0 |  |  |  |  | ( 2 X |  | ' L X | 0.4910 | R X | 0 | A ÷ 1,000 X |  | ) = |  | VD |  | ( |  | VD ÷ |  | V X 100 ) = |  | % VD
1 | SERVICE | 50 | 0.0085 | 1113 | 0.866 | 0.8 | 208 | 0.4 | ( 2 X | 50 | ' L X | 0.0085 | R X | 1,113 | A ÷ 1,000 X | 0.866 | ) = | 0.8 | VD | ( 2 X 50' L X 0.0085 R X 1,113 A ÷ 1,000 X 0.866 ) = 0.8 VD | ( | 0.8 | VD ÷ | 208 | V X 100 ) = | 0.4 | % VD | ( 0.8 VD ÷ 208 V X 100 ) = 0.4 % VD

## AFC (hidden)
28783
[18 empty] | PHASE |  | LENGTH
ACTIVE |  | PHASE | LENGTH | AFC | UA | MC | C | N | V | [7 empty] | ( | 2 | X | 30
1 | DP1 | 2 | 30 | 28783 | 1 | 0 | 4699 | 1 | 208 | 10403 | 10.4 | K | 10.4 K | (( | MC ) X | ( 1 ÷ ( 1 + | ( | 2.000 | X | 30 | L X (( | 28,783 | AFC X | 1.0 | UA ) + | 0.0 | MC )) ÷ ( | 4,699 | C X | 1 | N X | 208 | V ))) = | 10,403 | CLC | (( 28,783 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 28,783 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 4,699 C X 1 N X 208 V ))) = 10,403 CLC
1 | DP2 | 2 | 30 | 28783 | 1 | 0 | 4699 | 1 | 208 | 10403 | 10.4 | K | 10.4 K | (( | MC ) X | ( 1 ÷ ( 1 + | ( | 2.000 | X | 30 | L X (( | 28,783 | AFC X | 1.0 | UA ) + | 0.0 | MC )) ÷ ( | 4,699 | C X | 1 | N X | 208 | V ))) = | 10,403 | CLC | (( 28,783 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 28,783 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 4,699 C X 1 N X 208 V ))) = 10,403 CLC
1 | DP3 | 2 | 30 | 28783 | 1 | 0 | 4699 | 1 | 208 | 10403 | 10.4 | K | 10.4 K | (( | MC ) X | ( 1 ÷ ( 1 + | ( | 2.000 | X | 30 | L X (( | 28,783 | AFC X | 1.0 | UA ) + | 0.0 | MC )) ÷ ( | 4,699 | C X | 1 | N X | 208 | V ))) = | 10,403 | CLC | (( 28,783 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 28,783 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 4,699 C X 1 N X 208 V ))) = 10,403 CLC
0 | DP4 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP5 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP6 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP7 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP8 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP9 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP10 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP11 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP12 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP13 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP14 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP15 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP16 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP17 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP18 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP19 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP20 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP21 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP22 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP23 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP24 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP25 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP26 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP27 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP28 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP29 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
0 | DP30 | [5 empty] | 4699 | 1 | [5 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( | 4,699 | C X | 1 | N X |  | V ))) = |  | CLC | (( AFC X UA ) + MC ) X ( 1 ÷ ( 1 + ( X 30 L X (( AFC X UA ) + MC )) ÷ ( 4,699 C X 1 N X V ))) = CLC
1 | HP | 2 | 10 | 27892 | 1 | 0 | 2433 | 1 | 208 | 13267 | 13.3 | K | 13.3 K | (( | MC ) X | ( 1 ÷ ( 1 + | ( | 2.000 | X | 30 | L X (( | 27,892 | AFC X | 1.0 | UA ) + | 0.0 | MC )) ÷ ( | 2,433 | C X | 1 | N X | 208 | V ))) = | 13,267 | CLC | (( 27,892 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 27,892 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 2,433 C X 1 N X 208 V ))) = 13,267 CLC
0 | HSP | [12 empty] | (( | MC ) X | ( 1 ÷ ( 1 + | ( |  | X | 30 | L X (( |  | AFC X |  | UA ) + |  | MC )) ÷ ( |  | C X |  | N X |  | V ))) = |  | CLC
1 | SERVICE | 1.732 | 50 | 30000 | 1.1 | 0 | 18756 | 5 | 208 | 28783 | 28.8 | K | 28.8 K | (( | MC ) X | ( 1 ÷ ( 1 + | ( | 1.732 | X | 30 | L X (( | 30,000 | AFC X | 1.1 | UA ) + | 0.0 | MC )) ÷ ( | 18,756 | C X | 5 | N X | 208 | V ))) = | 28,783 | CLC | (( 30,000 AFC X 1.1 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 1.732 X 30 L X (( 30,000 AFC X 1.1 UA ) + 0.0 MC )) ÷ ( 18,756 C X 5 N X 208 V ))) = 28,783 CLC
33000

## Short (hidden)
| NO TRANSFORMER 3-PHASE Y |  |  |  | 30000 | 30000 | AUTO
|  | Available Fault Current at Starting Point |  |  | (( | 30000 | AFC x | 1.1 | UA ) + | 0 | MC ) = | 33000 | AFC
|  | Available Fault Current at Starting Point |  |  | (( | 30,000 | AFC X | 1.10 | UA ) + | 0 | MC ) = | 33,000 | AFC |  |  |  | (( 30,000 AFC X 1.10 UA ) + 0 MC ) = 33,000 AFC
33,000 AFC
Start > | < 33,000 AFC |  |  |  | < | 33,000 | AFC
[8 empty] | 0 | [5 empty] | 0.75 | 3/4"
| < 0' ' LENGTH |  |  |  | < | 0 | ' | LENGTH | [5 empty] | 1 | 1" | [7 empty] | feeder type | CONDUIT
| - 0 0 | [5 empty] | - | 0 |  | 0 |  |  |  | 1.25 | 1 1/4"
| 0 - 0 0 0 |  |  |  |  | 0 | - | 0 |  | 0 |  | 0 |  | 1.5 | 1 1/2" | [7 empty] | GENERAL | 0
| 0000 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 2 | 2" | [7 empty] | RIGID | 0
[14 empty] | 2.5 | 2 1/2" | [7 empty] | EMT | 1
[14 empty] | 3 | 3" | [7 empty] | IMC | 0
[14 empty] | 3.5 | 3 1/2" | [7 empty] | PVC-40 | 0
End > | < 28,776 AFC |  |  |  | < | 28,776 | AFC | [6 empty] | 4 | 4" | [7 empty] | RIGID/PVC | 0
[23 empty] | FLEX | 0
[23 empty] | LT-FLEX | 0
| Step 4 - Conductor Factor CF - Formula | [21 empty] | STELL=1 PLASTIC=2 | 1
| Three Phase | [21 empty] | CU=1 AL=2 | 2
Conductor Factor CF - Formula | ( | 1.732 | x | 50 | L x | 33000 | AFC ) ÷ ( | 18756 | C x | 5 | N x | 208 | V ) = | 0.147 |  | CF | Print
Conductor Factor CF - Formula | ( | 1.732 | X | 50 | L X | 33,000 | AFC ) ÷ ( | 18,756 | C X | 5 | N X | 208 | V ) = | 0.147 |  | CF | ( 1.732 X 50 L X 33,000 AFC ) ÷ ( 18,756 C X 5 N X 208 V ) = 0.147 CF | [5 empty] | TOTAL | 3
Step 5 - Conductor Multiplier CM - Formula
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.147 | CF ) = | 0.872 | CM | [7 empty] | Print
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.147 | CF ) = | 0.872 | CM | [7 empty] | ( 1 ) ÷ ( 1 + 0.147 CF ) = 0.872 CM
3
Step 6 - Conductor Let-Through Current CLC - Formula
Conductor Let-Through Current CLC - Formula | ( | 33000 | AFC X | 0.872 | CM ) = | 28776 | CLC | [9 empty] | Print | [5 empty] | 3 |  | 1 | 2 | 3 | 4 | 5 | 6
Conductor Let-Through Current CLC - Formula | ( | 33,000 | AFC X | 0.872 | CM ) = | 28,776 | CLC |  |  | 28,776 CLC | [6 empty] | ( 33,000 AFC X 0.872 CM ) = 28,776 CLC | [5 empty] | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit | SER-ROMEX | SER-ROMEX
[23 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | CABLE | CABLE
|  |  | Conductor Let-Through Current CLC - Formula ( 33,000 AFC X 0.872 CM ) = 28,776 CLC | [15 empty] | C7 | #500 | 18 |  | Cables AL |  | Cables CU | Cables CU | Cables AL | Cables AL | CU | AL
[18 empty] | #500 |  |  |  | 1 | 237 | #14 | 389 | 389 | 237 | 237 | 389 | 237
[18 empty] | ERROR |  |  |  | 2 | 376 | #12 | 617 | 617 | 376 | 376 | 617 | 376
[10 empty] | 28.8 | K | 28.8 K | [9 empty] | 3 | 599 | #10 | 981 | 982 | 599 | 599 | 982 | 599
[22 empty] | 4 | 951 | #8 | 1557 | 1559 | 951 | 952 | 1560 | 952
[22 empty] | 5 | 1481 | #6 | 2425 | 2430 | 1481 | 1482 | 2433 | 1482
[22 empty] | 6 | 2346 | #4 | 3806 | 3826 | 2346 | 2350 | 3838 | 2353
[22 empty] | 7 | 2952 | #3 | 4774 | 4811 | 2952 | 2961 | 4833 | 2966
[22 empty] | 8 | 3713 | #2 | 5907 | 6044 | 3713 | 3730 | 6087 | 3740
[21 empty] | 18 | 9 | 4645 | #1 | 7293 | 7493 | 4645 | 4678 | 7579 | 4699
[22 empty] | 10 | 5777 | #1/0 | 8925 | 9317 | 5777 | 5838 | 9473 | 5876
[22 empty] | 11 | 7187 | #2/0 | 10755 | 11424 | 7187 | 7301 | 11703 | 7373
[22 empty] | 12 | 8826 | #3/0 | 12844 | 13923 | 8826 | 9110 | 14410 | 9243
[22 empty] | 13 | 10741 | #4/0 | 15082 | 16673 | 10741 | 11174 | 17438 | 11409
[22 empty] | 14 | 12122 | #250 | 16483 | 18594 | 12122 | 12862 | 19779 | 13236
[22 empty] | 15 | 13910 | #300 | 18177 | 20868 | 13910 | 14923 | 22525 | 15495
[22 empty] | 16 | 15484 | #350 | 19704 | 22737 | 15484 | 16813 | 24904 | 17635
[22 empty] | 17 | 16671 | #400 | 20566 | 24297 | 16671 | 18506 | 26916 | 19588
[22 empty] | 18 | 18756 | #500 | 22185 | 26706 | 18756 | 21391 | 30096 | 23018
[22 empty] | 18756 | #500

## Calcs
[10 empty] | CODE YEAR | 2014
MULTIFAMILY SERVICE LOAD CALCULATIONS |  | PROJECT NAME | SAMPLE PROJECT |  | 0
BASED ON THE 2002 NEC SECTION 220.32 |  | MAIN PANEL | [27 empty] | 270000
[5 empty] | 0 | [24 empty] | 267000
FALSE |  | NEUTRAL LOAD PER NEC 220.61 |  |  | 0 | [24 empty] | 150000
TOTAL SQ FOOTAGE ( 45,000 SQ FT X 3 VA ) = | 135000 | TOTAL SQ FOOTAGE ( 45,000 SQ FT X 3 VA ) = |  | 135000 | 0 | 0
APPLIANCE CIRCUITS ( 60 X 1,500 VA ) = | 90000 | APPLIANCE CIRCUITS ( 60 X 1,500 VA ) = |  | 90000 | [13 empty] | PER PHASE DEMAND ( 23,000 ÷ 2 ) = 11,500 VA | [11 empty] | 3500
LAUNDRY CIRCUITS ( 30 X 1,500 VA ) = | 45000 | LAUNDRY CIRCUITS ( 30 X 1,500 VA ) = |  | 45000 | [13 empty] | EQUIVALENT 3-PHASE LOAD ( 11,500 X 3 ) =
|  | TOTAL CONNECTED NEUTRAL LOAD |  | 270000
[18 empty] | UNITS | 3 | 2
RANGES ( 20 ON ANY 2 PHASES ) = 160,000 KVA |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) = |  | 3000 |  | 1,200 | SQ FT X 3 VA = |  |  | 1,200 SQ FT X 3 VA = | [7 empty] | RANGES | 30 | 30 | [8 empty] | FIRST 3,000VA (100%) ( | 3000 | VA X 1.00 ) =
PER PHASE DEMAND ( 160,000 VA ÷ 2 ) = 80,000 VA |  | 3,000-120,000 VA @ 35% ( 120,000 VA X 0.35 ) = |  | 42000 |  | 2 | X 1,500 VA = |  |  | 2 X 1,500 VA = | [8 empty] | OK | [9 empty] | FIRST 3,000 VA @ 100% ( | 3,000 | VA X 1.00 ) = |  |  | FIRST 3,000 VA @ 100% ( 3,000 VA X 1.00 ) =
EQUIVALENT 3-PHASE LOAD ( 80,000 VA X 3 ) = | 240000 | OVER 120,000 VA @ 25% ( 150,000 VA X 0.25 ) = |  | 37500 |  | 1 | X 1,500 VA = |  |  | 1 X 1,500 VA = |  |  | NUMBER OF UNITS | 3 | 1 | 1
|  | SUBTOTAL |  | 82500 |  | 2 | X | 12,000 | VA = | 2 X 12,000 VA = |  |  |  |  | 2 | 1 | [12 empty] | 3,000-120,000 VA @ 35% ( | 120000 | VA X 0.35 ) = | 42000
[6 empty] | 1 | X | 5,000 | VA = | 1 X 5,000 VA = |  |  |  |  | 3 | 0.45 |  |  |  | 240000 | [8 empty] | 3,000-120,000 VA @ 35% ( | 120,000 | VA X 0.35 ) = |  |  | 3,000-120,000 VA @ 35% ( 120,000 VA X 0.35 ) = | [8 empty] | 600
DRYERS ( 20 ON ANY 2 PHASES ) = 150,000 KVA |  | RANGE DEMAND |  |  |  | 1 | X | 4,500 | VA = | 1 X 4,500 VA = |  |  |  |  | 4 | 0.45 | [8 empty] | 160000
PER PHASE DEMAND ( 100,000 VA ÷ 2 ) = 50,000 VA |  | PROHIBITED REDUCTION NEC 220.61(C)(1) | [12 empty] | 5 | 0.45 |  | RANGES | 30 | 20 | 20 | ( | 20 | ON ANY 2 PHASES ) = | 160,000 | KVA | RANGES ( 20 ON ANY 2 PHASES ) = 160,000 KVA |  | OVER 120,000 VA @ 25% ( | 150000 | VA X 0.25 ) = | 37500
EQUIVALENT 3-PHASE LOAD ( 50,000 VA X 3 ) = | 150000 | 100% OF TABLE 220.55 ( 45,000 VA X 1.00 ) = |  | 45000 | [10 empty] | 6 | 0.44 |  | PER PHASE DEMAND ( |  | 160000 | VA ÷ 2 ) = | 80000 | [6 empty] | OVER 120,000 VA @ 25% ( | 150,000 | VA X 0.25 ) = |  |  | OVER 120,000 VA @ 25% ( 150,000 VA X 0.25 ) =
[15 empty] | 7 | 0.44 |  | PER PHASE DEMAND ( |  | 160,000 | VA ÷ 2 ) = | 80,000 | VA |  |  |  | PER PHASE DEMAND ( 160,000 VA ÷ 2 ) = 80,000 VA
WATER HEATER LOAD | 75000 | DRYER DEMAND | [12 empty] | 8 | 0.43 |  | EQUIVALENT 3-PHASE LOAD ( |  |  | 80000 | VA X 3 ) = | 240000
MISC LOADS | 36000 | PROHIBITED REDUCTION NEC 220.61(C)(1) | [12 empty] | 9 | 0.43 |  | EQUIVALENT 3-PHASE LOAD ( |  |  | 80,000 | VA X 3 ) = |  |  |  |  | EQUIVALENT 3-PHASE LOAD ( 80,000 VA X 3 ) = | [12 empty] | CALCULATED LOAD | 1113 |  | 1e-08 | 0 | 100
LARGEST HEATING OR COOLING LOAD | 120000 | 100% OF TABLE 220.54 ( 150,000 VA 0.32 VA X 1.00 ) = |  | 47250 |  | MISC LOADS | 84139 | [7 empty] | 10 | 0.43 | [12 empty] | OVER 120,000 VA @ 25% ( 0 VA X 0.25 ) = | [10 empty] | MINIMUM AMPS | 1200 |  | 100 | 100 | 125
TOTAL CONNECTED LOAD | 891000 | [13 empty] | 11 | 0.42 | [26 empty] | 125 | 125 | 150
|  | UNBALANCED 120 VOLT MISC. LOADS AT 100% |  | 12000 |  | KVA | 891,000 | 2473.2413 | [6 empty] | 12 | 0.41 |  | NEC 220.84(A)(2) EXCEPTION | [21 empty] | MAX | 1200 |  | 150 | 150 | 175
CONNECTED AMPS ( 891,000 VA ÷ 208 V ÷ 1.732 ) = 2,473 A | [6 empty] | VA ÷ | [7 empty] | 13 | 0.41 | [26 empty] | 175 | 175 | 200
DEMAND FACTOR NEC TABLE 220.84 = 45% |  | NEUTRAL LOAD VA |  | 186750 |  |  | 208 | [7 empty] | 14 | 0.4 | [26 empty] | 200 | 200 | 225
ADJUSTED AMPS (2,473 A X 0.45 ) = | 1113 | [5 empty] | V | [7 empty] | 15 | 0.4 | [26 empty] | 225 | 225 | 250
HOUSE PANEL AMPS | 0 | NEUTRAL LOAD ( 186,750 VA ÷ 1.732 ÷ 208 V ) = |  | 518 |  |  | ÷ 1.732 ) = | [7 empty] | 16 | 0.39 | [12 empty] | 100% OF TABLE 220.55 ( | 45000 |  | 45,000 |  | VA X 1.00 ) = |  |  | 100% OF TABLE 220.55 ( 45,000 VA X 1.00 ) = | 45000 |  |  |  |  | 250 | 250 | 300
SUBTOTAL | 1113 | [5 empty] | ( | [7 empty] | 17 | 0.39 | [16 empty] | 0.315 | [9 empty] | 300 | 300 | 400
FUTURE FACTOR ( 1,113 A X 0.00 ) = | 0 | FURTHER DEMAND FACTOR - NEC 220.61(B)(2) | [12 empty] | 18 | 0.38 | [11 empty] | 100% OF TABLE 220.54 ( | 100% OF TABLE 220.54 ( | 150000 |  | 150,000 | 0.32 | VA X 1.00 ) = | VA |  | 100% OF TABLE 220.54 ( 150,000 VA 0.32 VA X 1.00 ) = | 47250 |  |  |  |  | 400 | 400 | 600
SERVICE SIZE | 1113 | FIRST 200 A @ 100% (200 A X 1.00 ) = |  | 200 |  |  | CONNECTED AMPS | [7 empty] | 19 | 0.38 |  | DRYERS | 30 | 20 | 20 | ( | 20 | ON ANY 2 PHASES ) = | 150,000 | KVA | DRYERS ( 20 ON ANY 2 PHASES ) = 150,000 KVA | [15 empty] | 600 | 600 | 800
|  | REMAINDER @ 70% ( 318 A X 0.70 ) = |  | 222.6 |  |  | 2,473 | [7 empty] | 20 | 0.38 |  | PER PHASE DEMAND ( |  | 100000 | VA ÷ 2 ) = | 50000 | [6 empty] | NEUTRAL LOAD ( | 186750 |  | 186,750 |  | VA ÷ 1.732 ÷ | 208 | V ) = | NEUTRAL LOAD ( 186,750 VA ÷ 1.732 ÷ 208 V ) = |  | 518 |  |  |  | 800 | 800 | 1000
[7 empty] | A | [7 empty] | 21 | 0.37 |  | PER PHASE DEMAND ( |  | 100,000 | VA ÷ 2 ) = | 50,000 | VA |  |  |  | PER PHASE DEMAND ( 100,000 VA ÷ 2 ) = 50,000 VA | [15 empty] | 1000 | 1000 | 1200
|  | MINIMUM NEUTRAL CONDUCTOR AMPACITY |  | 422.6 | [10 empty] | 22 | 0.36 |  | EQUIVALENT 3-PHASE LOAD ( |  |  | 50000 | VA X 3 ) = | 150000 | [19 empty] | 1200 | 1200 | 1600
[15 empty] | 23 | 0.36 |  | EQUIVALENT 3-PHASE LOAD ( |  |  | 50,000 | VA X 3 ) = |  |  |  |  | EQUIVALENT 3-PHASE LOAD ( 50,000 VA X 3 ) = | [15 empty] | 1600 | 1600 | 2000
[7 empty] | CONNECTED AMPS ( 891,000 VA ÷ 208 V ÷ 1.732 ) = 2,473 A | [7 empty] | 24 | 0.35 | [26 empty] | 2000 | 2000 | 2500
|  | VOLTAGE DROP CALCULATIONS |  |  | AUTO |  | 2473 | [7 empty] | 25 | 0.35 | [26 empty] | 2500 | 2500 | 3000
|  | ( 2 X 50' L X 0.0085 R X 1,113.0 A ÷ 1,000 X 0.866 ) = 0.8 VD | [12 empty] | 26 | 0.34 | [26 empty] | 3000 | 3000 | 4000
|  | ( 0.8 VD ÷ 208 V X 100 ) = 0.4 % VD | [12 empty] | 27 | 0.34
KEY | [14 empty] | 28 | 0.33 | [24 empty] | 1200 | A | 3-P
A - Amps |  | FAULT CURRENT CALCULATIONS | [11 empty] | 0 | 29 | 0.33 | [24 empty] | 1200 | A | 3-P |  | 1200A 3-P
AFC - Available Fault Current |  | (( 30,000 AFC X 1.10 UA ) + 0 MC ) = 33,000 AFC |  |  |  | FIRST 200 A @ 100% ( | 200 | A X 1.00 ) = | [5 empty] | 0.45 | 30 | 0.33
C - Conductor Constance |  | ( 1.732 X 50 L X 33,000 AFC ) ÷ ( 18,756 C X 5 N X 208 V ) = 0.147 CF |  |  |  | FIRST 200 A @ 100% ( | 200 | A X 1.00 ) = | FIRST 200 A @ 100% (200 A X 1.00 ) = |  |  |  |  | 0
CF - Conductor Factor |  | ( 1 ) ÷ ( 1 + 0.147 CF ) = 0.872 CM | [10 empty] | ( | 00
CLC - Conductor Let Through Current |  | ( 33,000 AFC X 0.872 CM ) = 28,776 CLC |  |  |  | REMAINDER @ 70% ( | 318 | A X 0.70 ) = |  |  |  |  | ) | A X |  |  | DEMAND FACTOR NEC TABLE 220.84 =
CM - Conductor Multiplier | [5 empty] | REMAINDER @ 70% ( | 318 | A X 0.70 ) = | REMAINDER @ 70% ( 318 A X 0.70 ) = |  |  |  |  | 0.45
L - Length | [13 empty] | = | [26 empty] | 1200 | A |  | 208 | / | 120 | V | 3-PHASE | 1200A 208/120V 3-PHASE
MC - Motor Contribution
N - Number of Conductors | [6 empty] | 0
R - Resistance | [6 empty] | 1 | [6 empty] | ( 00 A X 0.45 ) = |  |  | ADJUSTED AMPS (
UA - Utility Adjustment |  |  |  |  | FAULT | YES | 0 | [9 empty] | ADJUSTED AMPS (
V - Volts |  |  |  |  | VD | YES | 1 | ALL
VA - Volt Amps |  |  |  |  | FEEDER | AUTO
VD - Voltage Drop
[8 empty] | 1 | 2 | 3 | 4 | 5
[7 empty] | A - Amps | A - Amps | A - Amps | A - Amps | A - Amps | A - Amps | [7 empty] | 45 | % | DEMAND FACTOR NEC TABLE 220.84 = 45%
[7 empty] | AFC - Available Fault Current | AFC - Available Fault Current | AFC - Available Fault Current | VA - Volt Amps | L - Length | AFC - Available Fault Current
[7 empty] | C - Conductor Constance | C - Conductor Constance | C - Conductor Constance |  | R - Resistance | MC - Motor Contribution
[7 empty] | CF - Conductor Factor | CF - Conductor Factor | CF - Conductor Factor |  | VA - Volt Amps | UA - Utility Adjustment
[7 empty] | CLC - Conductor Let Through Current | CLC - Conductor Let Through Current | CLC - Conductor Let Through Current |  | VD - Voltage Drop | VA - Volt Amps
[7 empty] | CM - Conductor Multiplier | CM - Conductor Multiplier | CM - Conductor Multiplier | [8 empty] | 2473 | A X | 0.45 | ) = | 1113
[7 empty] | L - Length | L - Length | L - Length | [8 empty] | 2,473 | A X | 0.45 | ) = | ADJUSTED AMPS (2,473 A X 0.45 ) =
[7 empty] | MC - Motor Contribution | MC - Motor Contribution | MC - Motor Contribution
[7 empty] | N - Number of Conductors | N - Number of Conductors | N - Number of Conductors
[7 empty] | R - Resistance | R - Resistance | UA - Utility Adjustment | [7 empty] | FUTURE FACTOR ( | 1113 | A X | 0 | ) = | 0
[7 empty] | UA - Utility Adjustment | UA - Utility Adjustment | V - Volts | [7 empty] | FUTURE FACTOR ( | 1,113 | A X | 0.00 | ) = | FUTURE FACTOR ( 1,113 A X 0.00 ) =
[7 empty] | V - Volts | V - Volts | VA - Volt Amps
[7 empty] | VA - Volt Amps | VA - Volt Amps
[7 empty] | VD - Voltage Drop | VD - Voltage Drop | [13 empty] | AUTO
Prepared With Residential 1-Line 2026 Software - Copyright Durand & Associates

## Tables (hidden)
TABLE 220.55, FROM 2005 N.E.C.
|  | NUMBER |  |  | COLUMN C |  | COLUMN A |  | COLUMN B
|  | OF |  |  | NOT OVER 12 |  | LESS THAN 3.5 |  | 3.5 to 8.75
|  | APPLIANCES |  |  | KW RATING |  | KW RATING |  | KW RATING
|  | 1 | 1 | 0 | 8 | 0 | 80 | 0 | 80
NUMBER OF RANGES | 30 | 2 | 2 | 0 | 11 | 0 | 75 | 0 | 65
|  | 3 | 3 | 0 | 14 | 0 | 70 | 0 | 55
MAXIMUM DEMAND |  | 4 | 4 | 0 | 17 | 0 | 66 | 0 | 50
FROM COLUMN A |  | 5 | 5 | 0 | 20 | 0 | 62 | 0 | 45
TABLE 220-19 | 45 | 6 | 6 | 0 | 21 | 0 | 59 | 0 | 43
|  | 7 | 7 | 0 | 22 | 0 | 56 | 0 | 40
PERCENTAGE DEMAND |  | 8 | 8 | 0 | 23 | 0 | 53 | 0 | 36
FROM COLUMN B |  | 9 | 9 | 0 | 24 | 0 | 51 | 0 | 35
TABLE 220.55 | 0.3 | 10 | 10 | 0 | 25 | 0 | 49 | 0 | 34
|  | 11 | 11 | 0 | 26 | 0 | 47 | 0 | 32
PERCENTAGE DEMAND |  | 12 | 12 | 0 | 27 | 0 | 45 | 0 | 32
FROM COLUMN C |  | 13 | 13 | 0 | 28 | 0 | 43 | 0 | 32
TABLE 220.55 | 0.24 | 14 | 14 | 0 | 29 | 0 | 41 | 0 | 32
|  | 15 | 15 | 0 | 30 | 0 | 40 | 0 | 32
|  | 16 | 16 | 0 | 31 | 0 | 39 | 0 | 28
|  | 17 | 17 | 0 | 32 | 0 | 38 | 0 | 28
|  | 18 | 18 | 0 | 33 | 0 | 37 | 0 | 28
|  | 19 | 19 | 0 | 34 | 0 | 36 | 0 | 28
|  | 20 | 20 | 0 | 35 | 0 | 35 | 0 | 28
|  | 21 | 21 | 0 | 36 | 0 | 34 | 0 | 26
|  | 22 | 22 | 0 | 37 | 0 | 33 | 0 | 26
|  | 23 | 23 | 0 | 38 | 0 | 32 | 0 | 26
|  | 24 | 24 | 0 | 39 | 0 | 31 | 0 | 26
|  | 25 | 25 | 0 | 40 | 0 | 30 | 0 | 26
|  | 26-30 | 26 | 45 | 15 KW + 1KW | 0.3 | 30 | 0.24 | 24
|  | 31-40 | 31 |  | FOR EACH RANGE |  | 30 | 0 | 22
|  | 41-50 | 41 | 0 | 25 KW + .75 KW |  | 30 | 0 | 20
|  | 51-60 | 51 |  | FOR EACH |  | 30 | 0 | 18
|  | 61 & OVER | 61 |  | RANGE |  | 30 | 0 | 16
|  |  |  | 45 |  | 0.3 |  | 0.24
TABLE 220.54, FROM 2005 N.E.C.
|  | NUMBER |  |  | DEMAND
|  | OF |  |  | FACTOR
|  | DRYERS |  |  | PERCENT
NUMBER OF DRYERS | 30 | 1 | 1 | 0 | 100
|  | 2 | 2 | 0 | 100
DEMAND FACTOR | 31.5 | 3 | 3 | 0 | 100
|  | 4 | 4 | 0 | 100
|  | 5 | 5 | 0 | 85
|  | 6 | 6 | 0 | 75
|  | 7 | 7 | 0 | 65
|  | 8 | 8 | 0 | 60
|  | 9 | 9 | 0 | 55
|  | 10 | 10 | 0 | 50
|  | 11 | 11 | 0 | 47
|  | 12 | 12 | 0 | 46 |  | 46 | 46 | 0
|  | 13 | 13 | 0 | 45 |  | 45 | 45 | 0
|  | 14 | 14 | 0 | 44 |  | 44 | 44 | 0
|  | 15 | 15 | 0 | 43 |  | 43 | 43 | 0
|  | 16 | 16 | 0 | 42 |  | 42 | 42 | 0
|  | 17 | 17 | 0 | 41 |  | 41 | 41 | 0
|  | 18 | 18 | 0 | 40 |  | 40 | 40 | 0
|  | 19 | 19 | 0 | 39 |  | 39 | 39 | 0
|  | 20 | 20 | 0 | 38 |  | 38 | 38 | 0
|  | 21 | 21 | 0 | 37 |  | 37 | 37 | 0
|  | 22 | 22 | 0 | 36 |  | 36 | 36 | 0
|  | 23 | 23 | 0 | 35 |  | 35 | 35 | 0
|  | 24 | 24 | 0 | 34.5 |  | 34.5 | 34.5 | 0
|  | 25 | 25 | 0 | 34 |  | 34 | 34 | 0
|  | 26 | 26 | 0 | 33.5 |  | 33.5 | 33.5 | 0
|  | 27 | 27 | 0 | 33 |  | 33 | 33 | 0
|  | 28 | 28 | 0 | 32.5 |  | 32.5 | 32.5 | 0
|  | 29 | 29 | 0 | 32 |  | 32 | 32 | 0
|  | 30 | 30 | 31.5 | 31.5 |  | 31.5 | 31.5 | 0
|  | 31 | 31 | 0 | 31 |  | 31 | 31 | 0
|  | 32 | 32 | 0 | 30.5 |  | 30.5 | 30.5 | 0
|  | 33 | 33 | 0 | 30 |  | 30 | 30 | 0
|  | 34 | 34 | 0 | 29.5 |  | 29.5 | 29.5 | 0
|  | 35 | 35 | 0 | 29 |  | 29 | 29 | 0
|  | 36 | 36 | 0 | 28.5 |  | 28.5 | 28.5 | 0
|  | 37 | 37 | 0 | 28 |  | 28 | 28 | 0
|  | 38 | 38 | 0 | 27.5 |  | 27.5 | 27.5 | 0
|  | 39 | 39 | 0 | 27 |  | 27 | 27 | 0
|  | 40 | 40 | 0 | 26.5 |  | 26.5 | 26.5 | 0
|  | 41 | 41 | 0 | 26 |  | 26 | 26 | 0
|  | 42 | 42 | 0 | 25.5 |  | 25.5 | 25.5 | 0
|  | 43 & OVER | 43 | 0 | 25 |  | 25 |  | 99
31.5
RANGE ADD
5% PER KVA
OVER 12
| RANGE RATING |  | KVA
0
| 12 | 13 | 0.05
| 13 | 14 | 0.1
| 14 | 15 | 0.15
| 15 | 16 | 0.2
| 16 | 17 | 0.25
| 17 | 18 | 0.3
| 18 | 19 | 0.35
| 19 | 20 | 0.4
| 20 | 21 | 0.45
| 21 | 22 | 0.5
| 22 | 23 | 0.55
| 23 | 24 | 0.6
| 24 | 25 | 0.65
| 25 | 26 | 0.7
| 26 | 27 | 0.75
UNBALANCED LOAD
LOAD
| 1 |  |  |  |  | 0
| 2 | [5 empty] | 0
| 3 | [6 empty] | 0
| 4 |  |  |  |  | 0
| 5 | [5 empty] | 0
| 6 | [6 empty] | 0
| 7 |  |  |  |  | 0
| 8 | [5 empty] | 0
| 9 | [6 empty] | 0
| 10 |  |  |  |  | 0
| 11 | [5 empty] | 0
| 12 | [6 empty] | 0
| 13 |  |  |  |  | 0
| 14 | [5 empty] | 0
| 15 | [6 empty] | 0
| 16 |  |  |  |  | 0
| 17 | [5 empty] | 0
| 18 | [6 empty] | 0
| 19 |  |  |  |  | 0
| 20 | [5 empty] | 0
| 21 | [6 empty] | 0
| 22 |  |  |  |  | 0
| 23 | [5 empty] | 0
| 24 | [6 empty] | 0
|  | 0 | 0 |  |  | 0 | 0 | 0
0
0

## VD Calcs
VOLTAGE DROP CALCULATIONS |  | PROJECT NAME | SAMPLE PROJECT
[5 empty] | 0 | 0
FEEDER | VOLTAGE DROP |  |  | VOLTAGE DROP PERCENTAGE | 0
SERVICE POINT TO MAIN PANEL | ( 2 X 50' L X 0.0085 R X 1,113 A ÷ 1,000 X 0.866 ) = 0.8 VD |  |  | ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD
MAIN PANEL T0 HP1 | ( 2 X 10' L X 0.4910 R X 0 A ÷ 1,000 X 1 ) = 0.0 VD |  |  | ( 0.0 VD ÷ 208 V X 100 ) = 0.0 % VD | MAIN PANEL T0 | HP1 | MAIN PANEL T0 HP1 | 1
[5 empty] | MAIN PANEL T0 | HP2 | MAIN PANEL T0 HP2 | 0
MAIN PANEL T0 DP | ( 2 X 30' L X 0.2530 R X 98 A ÷ 1,000 X 1 ) = 1.5 VD |  |  | ( 1.5 VD ÷ 208 V X 100 ) = 0.7 % VD | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 1
MAIN PANEL T0 DP | ( 2 X 30' L X 0.2530 R X 98 A ÷ 1,000 X 1 ) = 1.5 VD |  |  | ( 1.5 VD ÷ 208 V X 100 ) = 0.7 % VD | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 1
MAIN PANEL T0 DP | ( 2 X 30' L X 0.2530 R X 98 A ÷ 1,000 X 1 ) = 1.5 VD |  |  | ( 1.5 VD ÷ 208 V X 100 ) = 0.7 % VD | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 1
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
[5 empty] | MAIN PANEL T0 | DP | MAIN PANEL T0 DP | 0
KEY
| A - Amps | R - Conductor Resistance
| L - Length | VD - Voltage Drop

## AFC Calcs
0
FAULT CURRENT CALCULATIONS |  | PROJECT NAME | SAMPLE PROJECT |  |  | 0 | 0
SERVICE POINT TO MAIN PANEL | (( 30,000 AFC X 1.1 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 1.732 X 30 L X (( 30,000 AFC X 1.1 UA ) + 0.0 MC )) ÷ ( 18,756 C X 5 N X 208 V ))) = 28,783 CLC |  |  |  |  | 30,000 | AFC | 30,000 AFC
MAIN PANEL T0 HP1 | (( 27,892 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 27,892 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 2,433 C X 1 N X 208 V ))) = 13,267 CLC | [7 empty] | MAIN PANEL T0 | HP1 | MAIN PANEL T0 HP1
[9 empty] | MAIN PANEL T0 | HP2 | MAIN PANEL T0 HP2
MAIN PANEL T0 DP | (( 28,783 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 28,783 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 4,699 C X 1 N X 208 V ))) = 10,403 CLC |  |  |  | 1 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
MAIN PANEL T0 DP | (( 28,783 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 28,783 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 4,699 C X 1 N X 208 V ))) = 10,403 CLC |  |  |  | 1 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
MAIN PANEL T0 DP | (( 28,783 AFC X 1.0 UA ) + 0.0 MC ) X ( 1 ÷ ( 1 + ( 2.000 X 30 L X (( 28,783 AFC X 1.0 UA ) + 0.0 MC )) ÷ ( 4,699 C X 1 N X 208 V ))) = 10,403 CLC |  |  |  | 1 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
[5 empty] | 0 |  |  |  | MAIN PANEL T0 | DP | MAIN PANEL T0 DP
KEY
AFC - Available Fault Current |  | L - Length |  | UA - Utility Adjustment
C - Conductor Constance |  | MC - Motor Contribution |  | V - Volts
CLC - Conductor Let Through Current |  | N - Number of Conductors

## Import (hidden)
|  |  |  | PANEL | PANEL | PANEL | CONDUCTOR | LENGTH | CONDUIT | WIRE 1 | WIRE 2 | WIRE 3 | WIRE 4 | VD | NUMBER | SQUARE | APPLIANCE | LAUNDRY | NUMBER | RANGE | NUMBER | DRYER | WATER | WATER | TOTAL | HEAT | HEAT | HEAT | HEAT | HEAT | HEAT | MAX | MISC | MAX | APP COUNT | APP KVA | APP COUNT | APP KVA | DRYER | WATER
# OF PANELS | 3 |  |  | NAME | PHASE | BREAKER | CONSTANT |  | CABLE | [5 empty] | OF | FOOTAGE | CIRCUITS | CIRCUITS | OF | KVA | OF | KVA | HEATER | HEATER | RANGE | 1 | 2 | 3 | 4 | 5 | 6 |  | LOADS | AMPS | YES | YES | NO | NO | TOTAL | HEATER
[6 empty] | SIZE | [8 empty] | CONDUCTORS |  |  |  | RANGES |  | DRYERS |  | NUMBER | KVA | KA | [8 empty] | HOUSE |  |  |  |  | KVA | KVA
|  | DWELLING | ERROR | 0 | [29 empty] | PANEL | [13 empty] | WIRE | AMPS
|  | PANELS | [45 empty] | RES
| 1 | 1 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 | 0 | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 1 | 30 | ' | 30' | 0.253 | 98
| 1 | 2 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 2 | 30 | ' | 30' | 0.253 | 98
| 1 | 3 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 3 | 30 | ' | 30' | 0.253 | 98
| 0 | 4 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 4 | 30 | ' | 30' | 0.253 | 98
| 0 | 5 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 5 | 30 | ' | 30' | 0.253 | 98
| 0 | 6 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 6 | 30 | ' | 30' | 0.253 | 98
| 0 | 7 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 7 | 30 | ' | 30' | 0.253 | 98
| 0 | 8 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 8 | 30 | ' | 30' | 0.253 | 98
| 0 | 9 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 9 | 30 | ' | 30' | 0.253 | 98
| 0 | 10 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 10 | 30 | ' | 30' | 0.253 | 98
| 0 | 11 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 11 | 30 | ' | 30' | 0.253 | 98
| 0 | 12 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 12 | 30 | ' | 30' | 0.253 | 98
| 0 | 13 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 13 | 30 | ' | 30' | 0.253 | 98
| 0 | 14 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 14 | 30 | ' | 30' | 0.253 | 98
| 0 | 15 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 15 | 30 | ' | 30' | 0.253 | 98
| 0 | 16 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 16 | 30 | ' | 30' | 0.253 | 98
| 0 | 17 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 17 | 30 | ' | 30' | 0.253 | 98
| 0 | 18 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 18 | 30 | ' | 30' | 0.253 | 98
| 0 | 19 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 19 | 30 | ' | 30' | 0.253 | 98
| 0 | 20 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 20 | 30 | ' | 30' | 0.253 | 98
| 0 | 21 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 21 | 30 | ' | 30' | 0.253 | 98
| 0 | 22 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 22 | 30 | ' | 30' | 0.253 | 98
| 0 | 23 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 23 | 30 | ' | 30' | 0.253 | 98
| 0 | 24 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 24 | 30 | ' | 30' | 0.253 | 98
| 0 | 25 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 25 | 30 | ' | 30' | 0.253 | 98
| 0 | 26 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 26 | 30 | ' | 30' | 0.253 | 98
| 0 | 27 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 27 | 30 | ' | 30' | 0.253 | 98
| 0 | 28 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 | 1200 |  |  | 28 | 30 | ' | 30' | 0.253 | 98
| 0 | 29 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  | 1200 |  | 29 | 30 | ' | 30' | 0.253 | 98
| 0 | 30 | 0 | DP | 1 | 100A-2P | 4699 | 30 | 1- SER CABLE | 3-#1 AL | 1-#3 GND |  |  | 0.7 % VD | 1 | 1500 | 2 | 1 | 1 | 8 | 1 | 5 | 1 | 2.5 | 8 | 1: 4000 | 4000 | 1200 |  | 0 | 0 | 0 | 0 | 5 | 2.5 |  |  | 1200 | 30 | 30 | ' | 30' | 0.253 | 98
[16 empty] | 45000 | 60 | 30 | 30 | 240 | 30 | 150 | 30 | 75 | 240 | 120000 | 0 | 0 | 0 | 0 | 0 | 120000 | 36000 |  | 0 | 0 | 0 | 0 | 150 | 75 | 12000 | 12000 | 12000
|  |  | 0 | [12 empty] | 135000 | 90000 | 45000 |  | 240000 |  | 150000 |  | 75000 | [14 empty] | 150000
[17 empty] | 60 | 30 | [7 empty] | 6: 120000
[16 empty] | 45,000 | X 1,500 VA ) = | X 1,500 VA ) = | UNITS TOTAL KVA = | 8000 |  | 5000 |  |  |  | 4: 0; 6: 120000
[16 empty] | SQ FT X 3 VA ) = | APPLIANCE CIRCUITS ( | LAUNDRY CIRCUITS ( |  | 20 |  | 20 |  | #DIV/0! |  | 4: 2500
[16 empty] | TOTAL SQ FOOTAGE ( |  |  |  | 160000 |  | 100000 |  |  |  | 4: 3
[16 empty] | TOTAL SQ FOOTAGE ( 45,000 SQ FT X 3 VA ) = | APPLIANCE CIRCUITS ( 60 X 1,500 VA ) = | LAUNDRY CIRCUITS ( 30 X 1,500 VA ) = | 30 UNITS TOTAL KVA = | [6 empty] | 4: 7500
[20 empty] | 160000 |  | 100000 | [18 empty] | 12000
[26 empty] | 4: FUTURE COOLING LOAD (; 6: 3 | UNITS X 2,500 VA ) = |  | FUTURE COOLING LOAD ( 3 UNITS X 2,500 VA ) =
[18 empty] | NUMBER OF DWELLING UNITS | 3 | [12 empty] | NUMBER OF DWELLING UNITS | 3
[18 empty] | COUNT | 3 | [12 empty] | AC UNITS | 30
[18 empty] | 1 | 1 | [12 empty] | 1 | 1 |  |  | YOUR SERVICE CONFIGURATION HAS
[18 empty] | 2 | 1 | [12 empty] | 2 | 1 |  | 3 | 3
[18 empty] | 3 | 1 |  |  | YOUR SERVICE CONFIGURATION HAS | [9 empty] | 3 | 1 |  |  | DWELLING UNITS AND EACH DWELLING HAS A HEATING
[18 empty] | 4 | 0 |  | 3 | 3 | [9 empty] | 4 | 1 |  |  | OR AIR CONDITIONING LOAD
[18 empty] | 5 | 0 |  |  | DWELLING UNITS AND EACH DWELLING HAS A RANGE | [9 empty] | 5 | 1
|  |  | 0 | [14 empty] | 6 | 0 | [12 empty] | 6 | 1 |  |  | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS AND EACH DWELLING HAS A HEATING
[18 empty] | 7 | 0 | [12 empty] | 7 | 1 |  |  | OR AIR CONDITIONING LOAD
[18 empty] | 8 | 0 |  |  | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS AND EACH DWELLING HAS A RANGE | [9 empty] | 8 | 1
[18 empty] | 9 | 0 |  |  | THIS MEETS THE REQUIREMENTS OF NEC 220.84(A)(2) EXCEPTION | [9 empty] | 9 | 1 |  |  | THIS MEETS THE REQUIREMENTS OF NEC 220.84(A)(3)
[18 empty] | 10 | 0 | [12 empty] | 10 | 1
[18 empty] | 11 | 0 | [12 empty] | 11 | 1
[18 empty] | 12 | 0 |  |  | YOUR SERVICE CONFIGURATION HAS | [9 empty] | 12 | 1
[18 empty] | 13 | 0 |  | 3 | 3 | [9 empty] | 13 | 1 |  |  | YOUR SERVICE CONFIGURATION HAS
[18 empty] | 14 | 0 |  |  | DWELLING UNITS, HOWEVER, ONLY | [9 empty] | 14 | 1 |  | 3 | 3
[18 empty] | 15 | 0 |  | 3 | 3 | [9 empty] | 15 | 1 |  |  | DWELLING UNITS, HOWEVER, ONLY
[18 empty] | 16 | 0 |  |  | OF THE DWELLINGS | [9 empty] | 16 | 1 |  | 30 | 30
[18 empty] | 17 | 0 | [12 empty] | 17 | 1 |  |  | OF THE DWELLINGS
[18 empty] | 18 | 0 | [12 empty] | 18 | 1
[18 empty] | 19 | 0 |  |  | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS, HOWEVER, ONLY 3 OF THE DWELLINGS | [9 empty] | 19 | 1
[18 empty] | 20 | 0 |  |  | HAVE A RANGE. CHECK EACH DWELLING AND MAKE SURE AT LEAST ONE (1) RANGE IS ENTERED | [9 empty] | 20 | 1 |  |  | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS, HOWEVER, ONLY 30 OF THE DWELLINGS
[18 empty] | 21 | 0 | [12 empty] | 21 | 1 |  |  | HAVE A HEATING OR AIR CONDITIONING LOADS. CHECK EACH DWELLING AND MAKE SURE EACH
[18 empty] | 22 | 0 |  |  | IF ANY OF THE DWELLINGS DO NOT HAVE A RANGE YOU WILL NEED TO ENTER 1 RANGE AT 8 KW. | [9 empty] | 22 | 1 |  |  | DWELLING HAS A HEATING OR AIR CONDITIONING LOAD.
[18 empty] | 23 | 0 |  |  | THIS WILL MEET THE REQUIREMENTS OF NEC 220.84(A)(2) EXCEPTION | [9 empty] | 23 | 1
[18 empty] | 24 | 0 | [12 empty] | 24 | 1 |  |  | IF ANY OF THE DWELLINGS DO NOT HAVE A HEATING OR AIR CONDITIONING LOAD YOU WILL NEED
[18 empty] | 25 | 0 | [12 empty] | 25 | 1 |  |  | TO ENTER A LOAD. THIS WILL MEET THE REQUIREMENTS OF NEC 220.84(A)(3)
[18 empty] | 26 | 0 | [12 empty] | 26 | 1
[18 empty] | 27 | 0 |  |  | YOUR SERVICE CONFIGURATION HAS | [9 empty] | 27 | 1
[18 empty] | 28 | 0 |  | 3 | 3 | [9 empty] | 28 | 1
[18 empty] | 29 | 0 |  |  | DWELLING UNITS AND NONE OF THE UNITS HAVE A RANGE. | [9 empty] | 29 | 1
[18 empty] | 30 | 0 | [12 empty] | 30 | 1
YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS AND NONE OF THE UNITS HAVE A RANGE.
[22 empty] | THE PROGRAM HAS AUTOMATICALLY APPLIED NEC 220.84(A)(2) EXCEPTION TO THE LOAD CALCULATIONS | [13 empty] | YOUR SERVICE CONFIGURATION HAS
[35 empty] | 3 | 3
DWELLING UNITS AND NONE OF THE UNITS HAVE A HEATING
[21 empty] | 0 | [14 empty] | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS AND NONE OF THE UNITS HAVE A HEATING
[22 empty] | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS AND EACH DWELLING HAS A RANGE | [13 empty] | OR AIR CONDITIONING LOAD. THE PROGRAM HAS AUTOMATICALLY CALCULATED A 2.5 KVA
[22 empty] | THIS MEETS THE REQUIREMENTS OF NEC 220.84(A)(2) EXCEPTION | [13 empty] | AIR CONDITIONING LOAD FOR ECAH DWELLING AND APPLIED THAT TO THE LOAD CALCULATIONS.
THIS MEETS THE REQUIREMENTS OF NEC 220.84(A)(3)
[20 empty] | CODE YEAR | 2014
1
[35 empty] | 1 | YOUR SERVICE CONFIGURATION HAS 3 DWELLING UNITS, HOWEVER, ONLY 30 OF THE DWELLINGS
HAVE A HEATING OR AIR CONDITIONING LOADS. CHECK EACH DWELLING AND MAKE SURE EACH
DWELLING HAS A HEATING OR AIR CONDITIONING LOAD.
IF ANY OF THE DWELLINGS DO NOT HAVE A HEATING OR AIR CONDITIONING LOAD YOU WILL NEED
TO ENTER A LOAD. THIS WILL MEET THE REQUIREMENTS OF NEC 220.84(A)(3)

## Update Check (hidden)
|  |  |  | HIGH | HIGH | UPDATE | LOW | LOW | UPDATE | PHASE | PHASE | UPDATE | FAULT | FAULT |  | FAULT | FAULT |  | VD | VD |  | CODE | CODE
# OF PANELS | 3 |  |  | VOLTS | VOLTS | CHECK | VOLTS | VOLTS | CHECK | OUT TO | IN FROM | CHECK | CURRENT | CURRENT |  | YES/NO | YES/NO |  | YES/NO | YES/NO |  | YEAR | YEAR
VD | YES |  |  | OUT TO | IN FROM |  | OUT TO | IN FROM |  | DWELLING | DWELLING |  | OUT TO | IN FROM |  | OUT TO | IN FROM |  | OUT TO | IN FROM |  | OUT TO | IN FROM
FAULT | YES | DWELLING |  | DWELLING | DWELLING |  | DWELLING | DWELLING |  | PANELS | PANELS |  | DWELLING | DWELLING |  | DWELLING | DWELLING |  | DWELLING | DWELLING |  | DWELLING | DWELLING
|  | PANELS |  | PANELS | PANELS |  | PANELS | PANELS |  |  |  |  | PANELS | PANELS |  | PANELS | PANELS |  | PANELS | PANELS |  | PANELS | PANELS
| 1 | 1 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 1 | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 1 | 2 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 1 | 3 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 4 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 5 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 6 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 7 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 8 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 9 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 10 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 11 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 12 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 13 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 14 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 15 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 16 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 17 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 18 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 19 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 20 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 21 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 22 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 23 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 24 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 25 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 26 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 27 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 28 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 29 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0
| 0 | 30 | 0 | 208 | 208 | 0 | 120 | 120 | 0 | 3Y | 3Y | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2008 | 2008 | 0

## 1-Line
ERROR | 0
MAIN BREAKER | YES |  | / | \
HOUSE PANEL | YES | 30 K | [5 empty] | 1200A 208/120V 3-PHASE
CIRCUITS | 3 |  |  | 50'
SYSTEM GROUND | YES |  |  | 5-2 1/2'' EMT | [5 empty] | HOUSE |  |  | UNIT 1 |  |  | UNIT 2 |  |  | UNIT 3 |  |  | UNIT 4 |  |  | UNIT 5 |  |  | UNIT 6 |  |  | UNIT 7 |  |  | UNIT 8 |  |  | UNIT 9 |  |  | UNIT 10
OVER/UNDER | OVERHEAD |  |  | 3-#500 THHN AL | [5 empty] | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER
FAULT CALCS | YES |  |  | 1-#1/0 THHN AL (N) |  | ( | 1200A 3-P
VD | YES | [8 empty] | ( | 60A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P
AUTO/MANUAL | AUTO | [9 empty] | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE
|  |  |  | 50' | 28.8 K | [5 empty] | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K
5-2 1/2'' EMT
|  |  |  | 3-#500 THHN AL | [6 empty] | 10' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30'
|  |  |  | 1-#1/0 THHN AL (N) |  |  | #4 CU - |  |  |  | 1- ROMEX |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE
[7 empty] | TO UFER |  |  |  | 3-#6 CU |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL
[7 empty] | GROUND |  |  |  | 1-#10 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND
|  |  | \ | /
[7 empty] | ___ | ___
[7 empty] | __ | __
[7 empty] | _ | _
[10 empty] | 13.3 K | 0.0 % VD |  | 10.4 K | 0.7 % VD |  | 10.4 K | 0.7 % VD |  | 10.4 K | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD
[12 empty] | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING
[9 empty] | HOUSE |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT
[9 empty] | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL
[9 empty] | HP1 |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP
HOUSE PANEL | YES
HOUSE SUB | NO
[13 empty] | UNIT 11 |  |  | UNIT 12 |  |  | UNIT 13 |  |  | UNIT 14 |  |  | UNIT 15 |  |  | UNIT 16 |  |  | UNIT 17 |  |  | UNIT 18 |  |  | UNIT 19 |  |  | UNIT 20
[13 empty] | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER
[13 empty] | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P
[14 empty] | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE
[14 empty] | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K
[14 empty] | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30'
[14 empty] | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE
[14 empty] | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL
[14 empty] | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND
[14 empty] | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD
[12 empty] | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING
[12 empty] | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT
[12 empty] | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL
[12 empty] | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP
[13 empty] | UNIT 21 |  |  | UNIT 22 |  |  | UNIT 23 |  |  | UNIT 24 |  |  | UNIT 25 |  |  | UNIT 26 |  |  | UNIT 27 |  |  | UNIT 28 |  |  | UNIT 29 |  |  | UNIT 30
[13 empty] | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER |  |  | METER
[13 empty] | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P |  | ( | 100A-2P
[14 empty] | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE |  |  | SINGLE PHASE
[14 empty] | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K |  |  | 28.8 K
[14 empty] | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30' |  |  | 30'
[14 empty] | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE |  |  | 1- SER CABLE
[14 empty] | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL |  |  | 3-#1 AL
[14 empty] | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND |  |  | 1-#3 GND
[14 empty] | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD |  |  | 0.7 % VD
[12 empty] | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING |  |  | DWELLING
[12 empty] | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT |  |  | UNIT
[12 empty] | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL |  |  | PANEL
[12 empty] | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP |  |  | DP