## Input
Mixed Use 1-Line 2014 (Ver 14.0A) - Copyright Durand & Associates | [5 empty] | Warning DO NOT use copy/paste commands with Panel | [9 empty] | LOAD CALCULATIONS FOR "PANEL | [63 empty] | # OF CONDUITS
[16 empty] | CP1 | [65 empty] | 1 1/4'' |  | RIGID | ( | 4 | - | #4 |  |  | 1 | - | CONDUIT | 1 - CONDUIT
PANEL |  | CP1 | [10 empty] | 0 | Y |  | " | [63 empty] | CONDUITS | 1 1/4'' | RIGID | [8 empty] | 1 1/4'' |  | RIGID | 1 1/4'' RIGID | [17 empty] | INPUT | RIGID
FED FROM |  | MAIN PANEL | [10 empty] | 0 | SIZE |  | LOAD CALCULATIONS FOR "PANEL CP1" | [48 empty] | #N/A |  |  | ERROR | [33 empty] | OVER CURRENT MODULE | [9 empty] | 1. GENERAL | 0 |  | CONDUIT SIZING MODULE
# OF CIRCUITS |  |  |  |  | 84 | [62 empty] | CODE |  | CELL NAME | [13 empty] | WIRE SIZE MODULE (4" MAX CONDUIT) | [27 empty] | 2. RIGID | 2
HI VOLTAGE |  |  |  |  | 240 |  | AFC AT THIS PANEL |  |  |  | 15,304 |  | 28875 | Y SIZE | [67 empty] | HI | NEUTRAL | CU/AL? | AL |  |  |  |  | WIRES | [11 empty] | FUSE SIZING AMPS | 57.9 | 0 | [7 empty] | 3. EMT | 0 |  | CONDUIT TYPE | 2
LOW VOLTAGE |  |  |  |  | 120 |  | FEEDER | [5 empty] | 3Y | [53 empty] | 1 | 0 | 0 | ENTER NUMBER OF CIRCUITS | [11 empty] | LEG | AMPS | WIRE TEMP | 75 |  | L2 AMPS |  | 57.9 | 1 | 57.9 | [10 empty] | # OF PHASE WIRES | 1 | [8 empty] | 4. IMC | 0 |  | WIRE AREA SQ IN | 0.3662
PHASE |  |  |  |  | 3Y |  | NUMBER OF CONDUITS |  |  |  | 1 |  | 0 | [53 empty] | 2 | 0 | 0 | 0 | [5 empty] | H VLOT | CHECK |  | SOURCE VOLTAGE IS 0V | DESIGN AMPS | 57.9 | 57.9 |  | DESIGN AMPS (NDA) | 57.9 |  | NEUTRAL AMPS |  | 0 | 1 | 0 | [20 empty] | 5. PVC-40 | 0 |  | PERCENT FILL | 0.4
FEEDER TYPE |  |  |  |  | CONDUIT |  | FEEDER CONDUIT |  |  |  | 1 1/4'' | [55 empty] | 3 | 0 | 0 | ERROR IN MAIN PANEL |  |  | ENTER LOW VOLTAGE |  |  | L VOLT | CHECK |  | SOURCE VOLTAGE IS 0V | MIN AMPS | 0 | 0 | 0 | LOOKUP AMPS | 57.9 |  | 33% OF PHASE |  | 21.7 | 1 | 21.7 | [20 empty] | 6. RIGID/PVC | 0
[5 empty] | FULL |  | WIRE SIZE L1 |  |  |  | #4 | [55 empty] | 4 | 0 | 0 | SELECT FEEDER TYPE | [11 empty] | 57.9 |  | NET Y/N | FULL | 4 | MAX |  | 21.7 |  | 21.7 | [10 empty] | LOOKUP | FUSE/BKR | [8 empty] | 7. FLEX | 0 |  | LOOKUP | 40% | CONDUIT | RIGID | CONDUIT |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
[5 empty] | 0 |  | WIRE SIZE L2 |  |  |  | #4 | [55 empty] | 5 | 0 | 0 | ENTER NEUTRAL SIZE | [5 empty] | MAIN PANEL PHASE |  | 3Y |  | CONNECTED LOAD | 15300 |  |  | HAR Y/N | N | 0 | [15 empty] | GROUND | AMP | [8 empty] | 8. LT-FLEX | 0 |  | TABLE | FILL | SIZE | AREA | SIZE |  | SIZE | GENERAL | RIGID | EMT | IMC | PVC-40 | RIGID/PVC | FLEX | LT-FLEX
GND WIRE Y/N |  |  |  |  | Y |  | WIRE SIZE L3 |  |  |  | #4 |  |  | KKK |  | NONE | [50 empty] | 6 | 0 | 0 | ENTER MINIMUM NET AMPS |  | MASTER | [5 empty] | 3Y |  | 50% CONNECTED | 7650 |  |  | SUBTOTAL |  | 4 | [15 empty] | AMPS | RATING | [8 empty] | OUTPUT | 2 |  |  |  |  | SQ IN |  |  |  | AREA | AREA | AREA | AREA | AREA | AREA | AREA | AREA
WIRE TYPE |  |  |  |  | THHN |  | WIRE SIZE NEUTRAL |  |  |  | #4 |  |  | KKK |  | 1-PHASE | [50 empty] | 7 | 0 | 0 | ENTER GROUND WIRE Y/N |  | ERROR | [5 empty] | 0 |  | HARMONIC LOAD | 0 | [20 empty] | 0 | 60 | [11 empty] | 0 | 0.1256 | 0.5 | 0.314 | 0.5 |  |  | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN
WIRE CU/AL? |  |  |  |  | AL |  | WIRE SIZE GROUND |  |  |  | #8 |  |  |  |  | 3-PHASE | [48 empty] | 84 |  | 8 | 0 | 0 | ENTER WIRE TYPE |  | 0 | 0 | 0 | [6 empty] | N | [20 empty] | 60 | 70 | [11 empty] | 0.1256 | 0.2196 | 0.75 | 0.549 | 0.75 |  | 0.5 | 0.285 | 0.314 | 0.304 | 0.342 | 0.285 | 0.304 | 0.317 | 0.314
WIRE TEMP ºC |  |  |  |  | 75 |  | SUB PANEL BKR |  |  |  | NONE | [55 empty] | 9 | 0 | 0 | ENTER WIRE CU/AL | [13 empty] | LOOKUP |  |  | ADJUST | SELECTED | WIRE | WIRE | WIRE | 60º C | 75 C | 90º C | AMPACITY TABLE | [6 empty] | 70 | 80 | [11 empty] | 0.2196 | 0.3552 | 1 | 0.888 | 1 |  | 0.75 | 0.508 | 0.549 | 0.533 | 0.586 | 0.508 | 0.533 | 0.533 | 0.541
WIRE LENGTH |  |  |  |  | 10 | [7 empty] | 0 | [53 empty] | 10 | 0 | 0 | ENTER WIRE TEMP | [13 empty] | WIRE |  |  | WIRE | WIRE | SIZE | SIZE | PER | AMPS | AMPS | AMPS | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | 80 | 90 | [11 empty] | 0.3552 | 0.6104 | 1.25 | 1.526 | 1.25 |  | 1 | 0.817 | 0.888 | 0.864 | 0.959 | 0.832 | 0.864 | 0.817 | 0.872
CONDUIT TYPE |  |  |  |  | RIGID | [61 empty] | 11 | 0 | 0 | ENTER WIRE LENGTH | [13 empty] | AMPS |  |  | AMPS | AMPS | AWG | CODE | PHASE | AL | AL | AL | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | 90 | 100 | [11 empty] | 0.6104 | 0.8284 | 1.5 | 2.071 | 1.5 |  | 1.25 | 1.277 | 1.526 | 1.496 | 1.646 | 1.453 | 1.495 | 1.277 | 1.528
MINIMUM AMPS |  |  |  |  | 0 | [61 empty] | 12 | 0 | 0 | ENTER CONDUIT TYPE | 1 | 0 | [11 empty] | 0 |  |  | 50 | 50 | #6 | 5 | 1 | 40 | 50 | 60 | AWG | CU | CU | CU | AL | AL | AL | 100 | 110 | [11 empty] | 0.8284 | 1.3632 | 2 | 3.408 | 2 |  | 1.5 | 1.857 | 2.071 | 2.036 | 2.223 | 1.986 | 2.036 | 1.857 | 1.979
[67 empty] | 13 | 0 | 0 | ENTER MINI AMPS | [13 empty] | 50 |  |  | 65 | 65 | #4 | 6 | 1 | 55 | 65 | 75 | #6 | 55 | 65 | 75 | 40 | 50 | 60 | 110 | 125 | [11 empty] | 1.3632 | 1.9464 | 2.5 | 4.866 | 2.5 |  | 2 | 3.245 | 3.408 | 3.356 | 3.629 | 3.291 | 3.355 | 3.269 | 3.245
# KITCHEN LOADS |  |  |  |  | 0 |  |  |  |  | DEMO VERSION | [56 empty] | 14 | 0 | 0 | ENTER MIN AMPS (L2) | [13 empty] | 65 |  |  | 75 | 75 | #4 | 6 | 1 | 65 | 75 | 85 | #4 | 70 | 85 | 95 | 55 | 65 | 75 | 125 | 150 | [11 empty] | 1.9464 | 2.9996 | 3 | 7.499 | 3 |  | 2.5 | 4.695 | 4.866 | 5.858 | 5.135 | 4.695 | 4.788 | 4.909 | 4.879
% FACTOR |  |  |  |  | 0 | [61 empty] | 15 | 0 | 0 | ENTER # OF KITCHEN LOADS | [13 empty] | 75 |  |  | 90 | 90 | #2 | 8 | 1 | 75 | 90 | 100 | #3 | 85 | 100 | 110 | 65 | 75 | 85 | 150 | 175 | [11 empty] | 2.9996 | 4.004 | 3.5 | 10.01 | 3.5 |  | 3 | 7.069 | 7.499 | 8.846 | 7.922 | 7.268 | 7.393 | 7.069 | 7.475
[67 empty] | 16 | 0 | 0 | ENTER % FACTOR | [13 empty] | 90 |  |  | 100 | 100 | #1 | 9 | 1 | 85 | 100 | 115 | #2 | 95 | 115 | 130 | 75 | 90 | 100 | 175 | 200 | [11 empty] | 4.004 | 5.1332 | 4 | 12.833 | 4 |  | 3.5 | 9.621 | 10.01 | 11.545 | 10.584 | 9.737 | 9.866 | 9.621 | 9.731
MAIN BKR / FUSE |  |  |  |  | Y | [45 empty] | DELTA | DELTA | DELTA | DELTA | 1-PHASE | 1-PHASE | 1-PHASE | 1-PHASE | 3-PHASE | 3-PHASE | 3-PHASE | 3-PHASE | 3-PHASE | 3-PHASE |  |  | 17 | 0 | 0 | ENTER % FACTOR L2 | [13 empty] | 100 |  |  | 120 | 120 | #1/0 | 10 | 1 | 100 | 120 | 135 | #1 | 110 | 130 | 150 | 85 | 100 | 115 | 200 | 225 | [17 empty] | 4 | 12.554 | 12.833 | 14.753 | 13.631 | 12.554 | 12.73 | 12.566 | 12.692
BREAKER SIZE |  |  |  |  | 60 | [8 empty] | ACTIVE | PHASE | CONNECTED | CONNECTED | CONNECTED | GENERAL | GENERAL | GENERAL | GENERAL | GENERAL | GENERAL | DIVERSITY | DIVERSITY | DIVERSITY | DIVERSITY | DIVERSITY | DIVERSITY | CONTINUOUS | CONTINUOUS | CONTINUOUS | CONTINUOUS | CONTINUOUS | CONTINUOUS | HARMONIC | HARMONIC | MOTOR | MOTOR | MOTOR | MOTOR | MOTOR | MOTOR | KITCHEN | KITCHEN | KITCHEN | KITCHEN | KITCHEN | KITCHEN | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL |  |  | 18 | 0 | 0 | ENTER MAIN BKR / FUSE | [13 empty] | 120 |  |  | 135 | 135 | #2/0 | 11 | 1 | 115 | 135 | 150 | #1/0 | 125 | 150 | 170 | 100 | 120 | 135 | 225 | 250 | [11 empty] | CONDUIT SIZE | 1.25 | DIFFERENT SIZE WIRES
[67 empty] | 19 | 0 | 0 | USE AL ON "-CA" WIRE | [13 empty] | 135 |  |  | 155 | 155 | #3/0 | 12 | 1 | 130 | 155 | 175 | #2/0 | 145 | 175 | 195 | 115 | 135 | 150 | 250 | 300 | [11 empty] | CONDUIT TYPE | RIGID
[14 empty] | CIRCUIT | LEG | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD |  |  | 20 | 0 | 0 | LOAD EXCEEDS 1,200 AMPS | [13 empty] | 155 |  |  | 180 | 180 | #4/0 | 13 | 1 | 150 | 180 | 205 | #3/0 | 165 | 200 | 225 | 130 | 155 | 175 | 300 | 350 | [11 empty] | CONDUIT SIZE | NOT USED | SAME SIZE WIRES
# | BKR | CIRCUIT DESCRIPTION | H | I |  |  | VA | I | H | CIRCUIT DESCRIPTION | BKR | # |  |  |  | L1 | L2 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | ODD CIR | EVEN CIR | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L3 | L3 | L1 | L1 | L2 | L2 | L1 | L1 | L2 | L2 | L3 | L3 |  |  | 21 | 0 | 0 | ENTER FAULT CURRENT CALCS METHOD > > | [13 empty] | 180 |  |  | 205 | 205 | #250 | 14 | 1 | 170 | 205 | 230 | #4/0 | 195 | 230 | 260 | 150 | 180 | 205 | 350 | 400 | [11 empty] | CONDUIT SIZE | 1.25 | DIFFERENT SIZE WIRES
1 |  |  |  | G | 6000 | L1 | 1100 | G |  | LIGHTS | 20A-1P | 2 |  | 1 | L1 | 7100 |  |  | 6000 | 1100 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 22 | 0 | 0 | ENTER AFC AT STARTING POINT | [13 empty] | 205 |  |  | 230 | 230 | #300 | 15 | 1 | 190 | 230 | 255 | #250 | 215 | 255 | 290 | 170 | 205 | 230 | 400 | 450 | [11 empty] | # OF WIRES | 5
3 |  |  |  | G | 6000 | L2 | 1100 | G |  | LIGHTS | 20A-1P | 4 |  | 1 | L2 |  | 7100 |  |  |  | 6000 | 1100 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 23 | 0 | 0 | ENTER UTILITY VOLTAGE ADJUSTMENT | [7 empty] | 3Y | [5 empty] | 230 |  |  | 250 | 250 | #350 | 16 | 1 | 210 | 250 | 280 | #300 | 240 | 285 | 320 | 190 | 230 | 255 | 450 | 500
5 |  |  |  | G |  | L3 | 1100 | G |  | LIGHTS | 20A-1P | 6 |  | 1 | L3 |  |  | 1100 |  |  |  |  | 0 | 1100 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 24 | 0 | 0 | ENTER PHASE |  |  | ENTER PHASE |  |  | PHASE | CHECK | 0 | SOURCE PHASE IS 3Y |  | CONDUIT SIZE | 1.25 |  | 250 |  |  | 270 | 270 | #400 | 17 | 1 | 225 | 270 | 305 | #350 | 260 | 310 | 350 | 210 | 250 | 280 | 500 | 600 | [18 empty] | 2: RIGID; 3: CONDUIT
7 |  |  |  | G |  | L1 |  | G |  |  |  | 8 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 25 | 0 | 0 | DELTA LOAD ERROR | [11 empty] | 1 1/4'' |  | 270 |  |  | 310 | 310 | #500 | 18 | 1 | 260 | 310 | 350 | #400 | 280 | 335 | 380 | 225 | 270 | 305 | 600 | 700 | [14 empty] | 2-WIRE | 3-WIRE | 4-WIRE |  | 2: AREA; 3: SIZE
9 |  |  |  | G |  | L2 |  | G |  |  |  | 10 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 26 | 0 | 0 | ENTER PANEL NAME | [11 empty] | 0 |  | 310 |  |  | 360 | 360 | #4/0 | 13 | 2 |  |  |  | #500 | 320 | 380 | 430 | 260 | 310 | 350 | 700 | 800 | [18 empty] | 2: SQ IN
11 |  |  |  | G |  | L3 |  | G |  |  |  | 12 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 27 | 0 | 0 | ENTER SOURCE | [11 empty] | 1 1/4'' |  | 360 |  |  | 410 | 410 | #250 | 14 | 2 | [10 empty] | 800 | 1000 | [11 empty] | 1 | 1 | ERR | 0 | 0 | 0 | 1.5243 | 1: 0.0824; 2: 0.1256; 3: 0.5
13 |  |  |  | G |  | L1 |  | G |  | PINK CELLS ARE |  | 14 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 28 | 0 | 0 | SELECT > > | [13 empty] | 410 |  |  | 460 | 460 | #300 | 15 | 2 | [10 empty] | 1000 | 1200 | [11 empty] | 2 | 2 | ERR | 2 | 0 | 0 | 2.665 | 1: 0.0824; 2: 0.2196; 3: 0.75
15 |  |  |  | G |  | L2 |  | G |  | PROTECTED IN DEMO |  | 16 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 30 | 0 | 0 | SHOW VD CALCS | [13 empty] | 460 |  |  | 500 | 500 | #350 | 16 | 2 | [23 empty] | 3 | 3 | ERR | 0 | 3 | 4 | 4.3107 | 1: 0.0824; 2: 0.3552; 3: 1
17 |  |  |  | G |  | L3 |  | G |  |  |  | 18 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  | 0 | [15 empty] | 500 |  |  | 540 | 540 | #400 | 17 | 2 | [23 empty] | 4 | 4 | ERR | 0 | 0 | 0 | 7.4078 | 1: 0.0824; 2: 0.6104; 3: 1.25
19 |  |  |  | G |  | L1 |  | G |  |  |  | 20 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [23 empty] | 540 |  |  | 620 | 620 | #500 | 18 | 2 | [10 empty] | UNDER 800A | 60 | #N/A | [10 empty] | 5 | 5 | ERR | 0 | 0 | 0 | 10.0534 | 1: 0.0824; 2: 0.8284; 3: 1.5
21 |  |  |  | G |  | L2 |  | G |  |  |  | 22 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 1 | 0 | 0 | ENTER CIRCUIT #1 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #1 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #1 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 620 |  |  | 690 | 690 | #300 | 15 | 3 | [10 empty] | OVER 800A |  | 0 | [10 empty] | 6 | 6 | ERR | 0 | 0 | 0 | 16.5437 | 1: 0.0824; 2: 1.3632; 3: 2
23 |  |  |  | G |  | L3 |  | G |  |  |  | 24 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 3 | 0 | 0 | ENTER CIRCUIT #3 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #3 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #3 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 690 |  |  | 750 | 750 | #350 | 16 | 3 | [10 empty] | RATING | 60 | [11 empty] | 7 | 7 | ERR | 0 | 0 | 0 | 23.6214 | 1: 0.0824; 2: 1.9464; 3: 2.5
25 |  |  |  | G |  | L1 |  | G |  |  |  | 26 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 5 | 0 | 0 | ENTER CIRCUIT #5 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #5 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #5 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 750 |  |  | 810 | 810 | #400 | 17 | 3 | [10 empty] | HI LEG FUSE | 0 | [11 empty] | 8 | 8 | ERR | 0 | 0 | 0 | 36.4029 | 1: 0.0824; 2: 2.9996; 3: 3
27 |  |  |  | G |  | L2 |  | G |  |  |  | 28 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 7 | 0 | 0 | ENTER CIRCUIT #7 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #7 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #7 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 810 |  |  | 930 | 930 | #500 | 18 | 3 | [23 empty] | 9 | 8 | ERR | 0 | 0 | 0 | 48.5922 | 1: 0.0824; 2: 4.004; 3: 3.5
29 |  |  |  | G |  | L3 |  | G |  |  |  | 30 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 9 | 0 | 0 | ENTER CIRCUIT #9 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #9 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #9 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 930 |  |  | 1000 | 1000 | #350 | 16 | 4 | [23 empty] | 10 | 10 | ERR | 0 | 0 | 0 | 62.2961 | 1: 0.0824; 2: 5.1332; 3: 4
31 |  |  |  | G |  | L1 |  | G |  |  |  | 32 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 11 | 0 | 0 | ENTER CIRCUIT #11 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #11 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #11 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1000 |  |  | 1080 | 1080 | #400 | 17 | 4 | [10 empty] | WIRE FILL SIZING MODULE
33 |  |  |  | G |  | L2 |  | G |  |  |  | 34 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 13 | 0 | 0 | ENTER CIRCUIT #13 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #13 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #13 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1080 |  |  | 1240 | 1240 | #500 | 18 | 4 | [11 empty] | L1 | [12 empty] | 54 | [5 empty] | 1: L2 RESISTANCE CALCULATION
35 |  |  |  | G |  | L3 |  | G |  |  |  | 36 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 15 | 0 | 0 | ENTER CIRCUIT #15 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #15 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #15 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1240 |  |  | 1250 | 1250 | #350 | 16 | 5 | [10 empty] | WIRE CODE (NPHC) | 6 | [12 empty] | 4
37 |  |  |  | G |  | L1 |  | G |  |  |  | 38 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 17 | 0 | 0 | ENTER CIRCUIT #17 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #17 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #17 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1250 |  |  | 1350 | 1350 | #400 | 17 | 5 | [10 empty] | WIRE TYPE (NWTYP) | THHN | [18 empty] | 1 | 1 | / | 0.508 | = | 0
39 |  |  |  | G |  | L2 |  | G |  |  |  | 40 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 19 | 0 | 0 | ENTER CIRCUIT #19 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #19 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #19 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1350 |  |  | 1550 | 1550 | #500 | 18 | 5 | [10 empty] | CU/AL ? | AL | [18 empty] | 2 | 1 | / | 0.508 | = | 0
41 |  |  |  | G |  | L3 |  | G |  |  |  | 42 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 21 | 0 | 0 | ENTER CIRCUIT #21 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #21 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #21 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1550 |  |  | 1620 | 1620 | #400 | 17 | 6 | [10 empty] | GND WIRE CODE | 4 | [18 empty] | 3 | 1 | / | 0.508 | = | 0
43 |  |  |  | G |  | L1 |  | G |  |  |  | 44 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 23 | 0 | 0 | ENTER CIRCUIT #23 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #23 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #23 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1620 |  |  | 1860 | 1860 | #500 | 18 | 6 | [10 empty] | NEUTRAL Y/N | FULL | 1 | [17 empty] | 4 | 1 | / | 0.508 | = | 0
45 |  |  |  | G |  | L2 |  | G |  |  |  | 46 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 25 | 0 | 0 | ENTER CIRCUIT #25 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #25 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #25 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [14 empty] | #OF WIRE | 3 | 3 | [17 empty] | 5 | 1 | / | 0.508 | = | 0
47 |  |  |  | G |  | L3 |  | G |  |  |  | 48 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 27 | 0 | 0 | ENTER CIRCUIT #27 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #27 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #27 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | SELECTED | WIRE | WIRE | WIRE | [14 empty] | TOTAL WIRES |  | 4 | [17 empty] | 6 | 1 | / | 0.508 | = | 0
49 |  |  |  | G |  | L1 |  | G |  |  |  | 50 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 29 | 0 | 0 | ENTER CIRCUIT #29 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #29 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #29 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | WIRE | SIZE | SIZE | PER | [14 empty] | GND WIRE CODE
51 |  |  |  | G |  | L2 |  | G |  |  |  | 52 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 31 | 0 | 0 | ENTER CIRCUIT #31 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #31 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #31 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | AMPS | AWG | CODE | PHASE | [27 empty] | VOLTAGE DROP MODULE | [6 empty] | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0
53 |  |  |  | G |  | L3 |  | G |  |  |  | 54 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 33 | 0 | 0 | ENTER CIRCUIT #33 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #33 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #33 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | L1-L3 | 65 | #4 | 6 | 1 |  | HI LEG | [12 empty] | WIRE | WIRE | ST |  | WIRE | WIRE | ST | ST | ST | ST | CA | CA | CA |  | 1-PHASE | 3Y | 3D | 3D
55 |  |  |  | G |  | L1 |  | G |  |  |  | 56 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 35 | 0 | 0 | ENTER CIRCUIT #35 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #35 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #35 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | L2 | 65 | #4 | 6 | 1 |  | 65 | #4 | 6 | [10 empty] | SIZE | SIZE | THHN |  | WIRE | WIRE | THW | RHW | THHN | XHHW | THW-CA | THHN-CA | XHHW-CA | CU/AL? | AL |  | HI LEG |  |  |  | 1: SINGLE CONDUCTOR; 8: 0.508
57 |  |  |  | G |  | L2 |  | G |  |  |  | 58 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 37 | 0 | 0 | ENTER CIRCUIT #37 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #37 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #37 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | NETURAL | 65 | #4 | 6 | 1 |  | 65 | #4 | 6 | [10 empty] | AWG | CODE | SIZE |  | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | ONE WAY DISTANCE | 10
59 |  |  |  | G |  | L3 |  | G |  |  |  | 60 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 39 | 0 | 0 | ENTER CIRCUIT #39 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #39 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #39 NEUTRAL IDENTIFIER ( N or SPACE ) | [27 empty] | SQ IN |  | AWG | CODE | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | TOTAL LOAD | 57.9 | 57.9 | 57.9 | 57.9 |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.508
61 |  |  |  | G |  | L1 |  | G |  |  |  | 62 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 41 | 0 | 0 | ENTER CIRCUIT #41 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #41 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #41 NEUTRAL IDENTIFIER ( N or SPACE ) | [12 empty] | NEUTRAL | [12 empty] | #10 | 3 | 0.0211 |  | #10 | 3 | 0.0333 | 0.0333 | 0.0211 | 0.0243 | 0.051 | 0.051 | 0.0394 | VOLTAGE | 240
63 |  |  |  | G |  | L2 |  | G |  |  |  | 64 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 43 | 0 | 0 | ENTER CIRCUIT #43 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #43 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #43 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | GROUND SIZE MODULE |  |  |  |  | 50 | #6 | 5 | [10 empty] | #8 | 4 | 0.0366 |  | #8 | 4 | 0.0556 | 0.0556 | 0.0366 | 0.0437 | 0.051 | 0.051 | 0.0394 | # OF PHASE WIRES | 1
65 |  |  |  | G |  | L3 |  | G |  |  |  | 66 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 45 | 0 | 0 | ENTER CIRCUIT #45 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #45 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #45 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | GND Y/N? (NGYN) | Y |  |  |  | 50 | #6 | 5 | [10 empty] | #6 | 5 | 0.0507 |  | #6 | 5 | 0.0726 | 0.1041 | 0.0507 | 0.059 | 0.066 | 0.0452 | 0.0394 | WIRE CODE | 6 | 6 | 6 | 6
67 |  |  |  | G |  | L1 |  | G |  |  |  | 68 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 47 | 0 | 0 | ENTER CIRCUIT #47 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #47 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #47 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | MAX AMPS (NMA) | 57.9 | [16 empty] | #4 | 6 | 0.0824 |  | #4 | 6 | 0.0973 | 0.1333 | 0.0824 | 0.0814 | 0.0881 | 0.073 | 0.053 | WIRE | WIRE | RES | RES | RES |  |  | 1: L1 & L2 RESISTANCE CALCULATION
69 |  |  |  | G |  | L2 |  | G |  |  |  | 70 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 49 | 0 | 0 | ENTER CIRCUIT #49 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #49 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #49 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | CU/AL? (NCUAL2) | AL | [16 empty] | #3 | 7 | 0.0973 |  | #3 | 7 | 0.1134 | 0.1521 | 0.0973 | 0.0962 |  |  |  | SIZE | SIZE | NEC | NEC | NEC
71 |  |  |  | G |  | L3 |  | G |  |  |  | 72 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 51 | 0 | 0 | ENTER CIRCUIT #51 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #51 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #51 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | GND_TABLE | [17 empty] | #2 | 8 | 0.1158 |  | #2 | 8 | 0.1333 | 0.175 | 0.1158 | 0.1146 | 0.1194 | 0.1017 | 0.073 | AWG | CODE | AL | CU | AL |  |  | 1 | 1 | / | 0.508 | = | 0
73 |  |  |  | G |  | L1 |  | G |  |  |  | 74 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 53 | 0 | 0 | ENTER CIRCUIT #53 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #53 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #53 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | LOOKUP |  | RATING | SEL | SEL |  | RATING | CU | CU | AL | AL | [7 empty] | #1 | 9 | 0.1562 |  | #1 | 9 | 0.1901 | 0.266 | 0.1562 | 0.1534 | 0.1698 | 0.1352 | 0.1017 | #6 | 5 | 0.808 | 0.491 | 0.808 |  |  | 2 | 1 | / | 0.508 | = | 0
75 |  |  |  | G |  | L2 |  | G |  |  |  | 76 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 55 | 0 | 0 | ENTER CIRCUIT #55 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #55 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #55 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | GROUND |  | OVER | WIRE | WIRE |  | OVER | WIRE | WIRE | WIRE | WIRE | [7 empty] | #1/0 | 10 | 0.1855 |  | #1/0 | 10 | 0.2223 | 0.3039 | 0.1855 | 0.1825 | 0.1963 | 0.159 | 0.1352 | #4 | 6 | 0.508 | 0.308 | 0.508 |  |  | 3 | 1 | / | 0.508 | = | 0
77 |  |  |  | G |  | L3 |  | G |  |  |  | 78 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 57 | 0 | 0 | ENTER CIRCUIT #57 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #57 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #57 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | AMPS |  | CURRENT | SIZE | CODE |  | CURRENT | SIZE | CODE | SIZE | CODE | [7 empty] | #2/0 | 11 | 0.2223 |  | #2/0 | 11 | 0.2624 | 0.3505 | 0.2223 | 0.219 | 0.2332 | 0.1924 | 0.159 | #3 | 7 | 0.403 | 0.245 | 0.403 |  |  | 4 | 1 | / | 0.508 | = | 0
79 |  |  |  | G |  | L1 |  | G |  |  |  | 80 |  | 1 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 59 | 0 | 0 | ENTER CIRCUIT #59 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #59 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #59 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 0 |  | 60 | #8 | 4 |  | 60 | #10 | 3 | #8 | 4 | [7 empty] | #3/0 | 12 | 0.2679 |  | #3/0 | 12 | 0.3117 | 0.4072 | 0.2679 | 0.2642 | 0.2733 | 0.229 | 0.1885 | #2 | 8 | 0.319 | 0.194 | 0.319 |  |  | 5 | 1 | / | 0.508 | = | 0
81 |  |  |  | G |  | L2 |  | G |  |  |  | 82 |  | 1 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 61 | 0 | 0 | ENTER CIRCUIT #61 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #61 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #61 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 60 |  | 100 | #6 | 5 |  | 100 | #8 | 4 | #6 | 5 | [7 empty] | #4/0 | 13 | 0.3237 |  | #4/0 | 13 | 0.3718 | 0.4754 | 0.3237 | 0.3197 | 0.3267 | 0.278 | 0.229 | #1 | 9 | 0.253 | 0.154 | 0.253 |  |  | 6 | 1 | / | 0.508 | = | 0
83 |  |  |  | G |  | L3 |  | G |  |  |  | 84 |  | 1 | L3 |  |  | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 63 | 0 | 0 | ENTER CIRCUIT #63 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #63 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #63 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 100 |  | 200 | #4 | 6 |  | 200 | #6 | 5 | #4 | 6 | [7 empty] | #250 | 14 | 0.397 |  | #250 | 14 | 0.4596 | 0.6291 | 0.397 | 0.3904 | 0.4128 | 0.3525 | 0.2733 | #1/0 | 10 | 0.201 | 0.122 | 0.201
[67 empty] | 65 | 0 | 0 | ENTER CIRCUIT #65 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #65 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #65 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 200 |  | 300 | #2 | 8 |  | 300 | #4 | 6 | #2 | 8 | [7 empty] | #300 | 15 | 0.4608 |  | #300 | 15 | 0.5281 | 0.7088 | 0.4608 | 0.4536 | 0.4717 | 0.4071 | 0.3421 | #2/0 | 11 | 0.159 | 0.0967 | 0.159 |  |  | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0
Mixed Use 1-Line 2014 (Ver 14.0A) - Copyright Durand & Associates | [5 empty] | Warning DO NOT use copy/paste commands with Panel | [33 empty] | MAX |  | MAX |  | MAX | [6 empty] | DELTA |  | DELTA |  | 1-PHASE |  | 1-PHASE |  | 3-PHASE |  | 3-PHASE |  | 3-PHASE |  |  |  | 67 | 0 | 0 | ENTER CIRCUIT #67 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #67 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #67 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 300 |  | 400 | #1 | 9 |  | 400 | #3 | 7 | #1 | 9 | [7 empty] | #350 | 16 | 0.5242 |  | #350 | 16 | 0.5958 | 0.787 | 0.5242 | 0.5166 | 0.5281 | 0.4656 | 0.4015 | #3/0 | 12 | 0.126 | 0.0766 | 0.126
[16 empty] | CONNECTED | CONNECTED | CONNECTED |  | GENERAL |  | GENERAL |  | GENERAL |  | DIVERSITY |  | DIVERSITY |  | DIVERSITY |  | CONTINUOUS |  | CONTINUOUS |  | CONTINUOUS |  | TOTAL |  | MOTOR |  | MOTOR |  | MOTOR | KITCHEN |  | KITCHEN |  | KITCHEN |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  |  |  | 69 | 0 | 0 | ENTER CIRCUIT #69 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #69 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #69 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 400 |  | 500 | #1/0 | 10 |  | 500 | #2 | 8 | #1/0 | 10 | [7 empty] | #400 | 17 | 0.5863 |  | #400 | 17 | 0.6619 | 0.8626 | 0.5863 | 0.5782 | 0.5876 | 0.5216 | 0.4536 | #4/0 | 13 | 0.1 | 0.0608 | 0.1 |  |  | 1: SINGLE CONDUCTOR; 8: 0.508
[16 empty] | LOAD | LOAD | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | HARMONIC |  | LOAD |  | LOAD |  | LOAD | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  |  |  | 71 | 0 | 0 | ENTER CIRCUIT #71 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #71 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #71 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 500 |  | 600 | #2/0 | 11 |  | 600 | #1 | 9 | #2/0 | 11 | [7 empty] | #500 | 18 | 0.7073 |  | #500 | 18 | 0.7901 | 1.0082 | 0.7073 | 0.6984 | 0.6939 | 0.6151 | 0.5026 | #250 | 14 | 0.0847 | 0.0515 | 0.0847
[16 empty] | L1 | L2 | L3 |  | L1 |  | L2 |  | L3 |  | L1 |  | L2 |  | L3 |  | L1 |  | L2 |  | L3 |  | LOAD |  | L1 |  | L2 |  | L3 | L1 |  | L2 |  | L3 |  | L1 |  | L3 |  | L1 |  | L2 |  | L1 |  | L2 |  | L3 |  |  |  | 73 | 0 | 0 | ENTER CIRCUIT #73 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #73 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #73 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 600 |  | 800 | #3/0 | 12 |  | 800 | #1/0 | 10 | #3/0 | 12 | [20 empty] | #300 | 15 | 0.0707 | 0.0429 | 0.0707 |  |  | 1: CALCULATED RESISTANCE OF CONDUCTOR(S); 8: 0.508
[16 empty] | 7100 | 7100 | 1100 |  | 7100 |  | 7100 |  | 1100 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 75 | 0 | 0 | ENTER CIRCUIT #75 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #75 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #75 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 800 |  | 1000 | #4/0 | 13 |  | 1000 | #2/0 | 11 | #4/0 | 13 | [7 empty] | L1-L3 WIRE CODE | 6 |  | L1,L3 | L2 | NET | # OF WIRES | [6 empty] | #350 | 16 | 0.0605 | 0.0367 | 0.0605
[40 empty] | 0 |  | 0 |  | 0 | [22 empty] | 77 | 0 | 0 | ENTER CIRCUIT #77 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #77 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #77 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | 1000 |  | 1200 | #250 | 14 |  | 1200 | #3/0 | 12 | #250 | 14 | [7 empty] | L1-L3 SQ IN | 0.0824 | X | 2 | 1 | 1 | 4 | = | 0.3296 | 0.0824 | 0 | 1 | #4 | #400 | 17 | 0.0529 | 0.0321 | 0.0529
[30 empty] | 0 |  | CONTINUOUS | [7 empty] | MAX | LINE LOAD | 0 | [6 empty] | TOTAL |  |  |  | 0 |  |  |  | 0 | [5 empty] | 0 |  |  |  | 79 | 0 | 0 | ENTER CIRCUIT #79 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #79 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #79 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | OUTPUT | OUTPUT | OUTPUT | OUTPUT | [14 empty] | L2 WIRE CODE | 6 | [11 empty] | #500 | 18 | 0.0424 | 0.0258 | 0.0424
[18 empty] | 15300 | [5 empty] | 15300 | [7 empty] | LOAD | [8 empty] | X | 3 |  | TOTAL |  |  |  |  | KITCHEN | [17 empty] | 81 | 0 | 0 | ENTER CIRCUIT #81 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #81 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #81 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | GROUND | WIRE | WIRE | WIRE | [14 empty] | L2 SQ IN | 0.0824 | X |  | 0 |  | 0 | = | 0 | 0.0824 | 0 | 3 | #4 | WIRE CODE | 6 | 6 | 6 | 6
[32 empty] | 0 | [9 empty] | 0 |  | MOTOR |  |  |  |  | LOAD | [17 empty] | 83 | 0 | 0 | ENTER CIRCUIT #83 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #83 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #83 NEUTRAL IDENTIFIER ( N or SPACE ) | [7 empty] | MAX | SIZE | SIZE | PER | [14 empty] | NET WIRE CODE | 6 | [11 empty] | WIRE RES | 0.508 | 0.508 | 0.508 | 0.508
[32 empty] | VA X .025 = | [11 empty] | LOAD |  |  |  |  | 0 | [11 empty] | NEUTRAL LOAD >> |  | 0 |  |  |  | 84 | 0 | 0 | CONNECTED ON (L2) LOAD MAY NOT EXCEED LOAD ON (L1 & L3) | [13 empty] | OVER CURRENT | AWG | CODE | PHASE | [14 empty] | NET SQ IN | 0.0824 | X |  |  | 0 | 0 | = | 0 | 0.0824 | 0 | 4 | #4 | AMPS PER WIRE | 57.9 | 57.9 | 57.9 | 57.9
[32 empty] | CONTINUOUS LOAD 0 VA X .025 = | [9 empty] | 0 |  | 0 | [21 empty] | 0 |  | 0 |  |  | 0 |  |  | 0 | [9 empty] | 60 | #8 | 4 | 1 | [14 empty] | GND WIRE CODE | 4
[102 empty] | GND SQ IN | 0.0366 | X |  |  |  | 1 | = | 0.0366 | 0.0366 | 5 | 0 | #8
[67 empty] | 2 | 0 | 0 | ENTER CIRCUIT #2 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #2 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #2 NEUTRAL IDENTIFIER ( N or SPACE )
[67 empty] | 4 | 0 | 0 | ENTER CIRCUIT #4 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #4 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #4 NEUTRAL IDENTIFIER ( N or SPACE ) | [25 empty] | TOTAL AREA OF CONDUCTORS | [5 empty] | 5 |  | 0.3662 |  | 5 | 8 | [8 empty] | 3: ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 ) = 0.6 VD
[67 empty] | 6 | 0 | 0 | ENTER CIRCUIT #6 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #6 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #6 NEUTRAL IDENTIFIER ( N or SPACE )
[67 empty] | 8 | 0 | 0 | ENTER CIRCUIT #8 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #8 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #8 NEUTRAL IDENTIFIER ( N or SPACE ) | [31 empty] | AL | (L2) | (N)
[67 empty] | 10 | 0 | 0 | ENTER CIRCUIT #10 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #10 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #10 NEUTRAL IDENTIFIER ( N or SPACE ) | [27 empty] | 4 | - | #4 |  | THHN | 4-#4 THHN AL | [8 empty] | 3D | 3D |  |  | 5: VD %; 6: VD %; 7: VD %; 8: VD %
[67 empty] | 12 | 0 | 0 | ENTER CIRCUIT #12 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #12 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #12 NEUTRAL IDENTIFIER ( N or SPACE ) | [27 empty] | 0 | - |  |  | THHN | [7 empty] | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3-PHASE Y | L2 | L1 & L3
[67 empty] | 14 | 0 | 0 | ENTER CIRCUIT #14 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #14 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #14 NEUTRAL IDENTIFIER ( N or SPACE ) | [27 empty] | 0 | - |  |  | THHN | [6 empty] | 2 | 2 | 2 | 2 | 2 | ( | ( | bar: 1 to 8
[67 empty] | 16 | 0 | 0 | ENTER CIRCUIT #16 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #16 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #16 NEUTRAL IDENTIFIER ( N or SPACE ) | [27 empty] | 1 | - | #8 |  | GND | 1-#8 AL GND | [5 empty] | X L | 10 | 10 | 10 | 10 | 2 | 2 | 2 | 2 | 2 | VD | 0.6 | 0.5 | 0.5 | 0.6
[67 empty] | 18 | 0 | 0 | ENTER CIRCUIT #18 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #18 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #18 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | X R | 0.508 | 0.508 | 0.508 | 0.508 | X | X | X | X | X | ÷ | VD ÷ | VD ÷ | VD ÷ | VD ÷
[67 empty] | 20 | 0 | 0 | ENTER CIRCUIT #20 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #20 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #20 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | X I | 57.9 | 57.9 | 57.9 | 57.9 | L | 10 | 10 | 10 | 10 | VOLTS | 240 | 240 | 240 | 240
[67 empty] | 22 | 0 | 0 | ENTER CIRCUIT #22 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #22 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #22 NEUTRAL IDENTIFIER ( N or SPACE ) | [32 empty] | 4-#4 THHN AL | [5 empty] | = |  |  |  |  | X | ' L X | ' L X | ' L X | ' L X | X | V X | V X | V X | V X
[67 empty] | 24 | 0 | 0 | ENTER CIRCUIT #24 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #24 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #24 NEUTRAL IDENTIFIER ( N or SPACE ) | [32 empty] | 1-#8 AL GND | [5 empty] | ÷ 1000 | 1000 | 1000 | 1000 | 1000 | R | 0.5080 | 0.5080 | 0.5080 | 0.5080 | 100 | 100 | 100 | 100 | 100
[67 empty] | 26 | 0 | 0 | ENTER CIRCUIT #26 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #26 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #26 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | = |  |  |  |  | X | R X | R X | R X | R X | ) = | ) = | ) = | ) = | ) =
[67 empty] | 28 | 0 | 0 | ENTER CIRCUIT #28 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #28 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #28 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | X 0.866 | 1 | 0.866 | 0.866 | 1 | I | 57.9 | 57.9 | 57.9 | 57.9 | VD | 0.3 | 0.2 | 0.2 | 0.3
[67 empty] | 30 | 0 | 0 | ENTER CIRCUIT #30 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #30 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #30 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | = VD | 0.6 | 0.5 | 0.5 | 0.6 | / | A ÷ | A ÷ | A ÷ | A ÷ | % | % VD | % VD | % VD | % VD
[67 empty] | 32 | 0 | 0 | ENTER CIRCUIT #32 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #32 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #32 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | ÷ VOLTS | 240 | 240 | 240 | 240 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | ( VD ÷ VOLTS X 100 ) = VD % | ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD | ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD | ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD | ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD
[67 empty] | 34 | 0 | 0 | ENTER CIRCUIT #34 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #34 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #34 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | = VD % | 0.25% | 0.21% | 0.21% | 0.25% | X | ) | X | X | ) |  | 0.3 % VD | 0.2 % VD | 0.2 % VD | 0.3 % VD
[67 empty] | 36 | 0 | 0 | ENTER CIRCUIT #36 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #36 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #36 NEUTRAL IDENTIFIER ( N or SPACE ) | [43 empty] | 0.866 | = | 1: 0.866; 2: 0.866; 3: =
[67 empty] | 38 | 0 | 0 | ENTER CIRCUIT #38 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #38 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #38 NEUTRAL IDENTIFIER ( N or SPACE ) | [43 empty] | ) | 0.6 | 1: ); 2: ); 3: 0.6
[67 empty] | 40 | 0 | 0 | ENTER CIRCUIT #40 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #40 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #40 NEUTRAL IDENTIFIER ( N or SPACE ) |  |  |  |  | FEEDER CONDUIT | [38 empty] | = | VD | bar: 1 to 3
[67 empty] | 42 | 0 | 0 | ENTER CIRCUIT #42 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #42 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #42 NEUTRAL IDENTIFIER ( N or SPACE ) | [43 empty] | VD |  | 1: 0.5; 2: 0.5
[67 empty] | 44 | 0 | 0 | ENTER CIRCUIT #44 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #44 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #44 NEUTRAL IDENTIFIER ( N or SPACE ) |  |  |  |  | 0 | bar: 1 to 2
[67 empty] | 46 | 0 | 0 | ENTER CIRCUIT #46 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #46 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #46 NEUTRAL IDENTIFIER ( N or SPACE )
[67 empty] | 48 | 0 | 0 | ENTER CIRCUIT #48 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #48 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #48 NEUTRAL IDENTIFIER ( N or SPACE ) | [44 empty] | 0.6 VD | 1: 0.5 VD; 2: 0.5 VD; 3: 0.6 VD
[67 empty] | 50 | 0 | 0 | ENTER CIRCUIT #50 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #50 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #50 NEUTRAL IDENTIFIER ( N or SPACE ) | [44 empty] | ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 ) = 0.6 VD | 1: ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 X 0.866 ) = 0.5 VD; 2: ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 X 0.866 ) = 0.5 VD; 3: ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 ) = 0.6 VD
[67 empty] | 52 | 0 | 0 | ENTER CIRCUIT #52 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #52 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #52 NEUTRAL IDENTIFIER ( N or SPACE )
[67 empty] | 54 | 0 | 0 | ENTER CIRCUIT #54 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #54 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #54 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | WIRE | WIRE
[67 empty] | 56 | 0 | 0 | ENTER CIRCUIT #56 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #56 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #56 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | SIZE | WIRE
[67 empty] | 58 | 0 | 0 | ENTER CIRCUIT #58 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #58 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #58 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | CODE | SIZE
[67 empty] | 60 | 0 | 0 | ENTER CIRCUIT #60 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #60 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #60 NEUTRAL IDENTIFIER ( N or SPACE ) | [36 empty] | AWG
[67 empty] | 62 | 0 | 0 | ENTER CIRCUIT #62 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #62 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #62 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 3 | #10
[67 empty] | 64 | 0 | 0 | ENTER CIRCUIT #64 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #64 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #64 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 4 | #8
[67 empty] | 66 | 0 | 0 | ENTER CIRCUIT #66 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #66 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #66 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 5 | #6 | [5 empty] | VOLTAGE DROP
[67 empty] | 68 | 0 | 0 | ENTER CIRCUIT #68 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #68 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #68 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 6 | #4 | [5 empty] | Single Phase | ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 ) = 0.6 VD |  | 2: Voltage Drop %; 3: ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD
[67 empty] | 70 | 0 | 0 | ENTER CIRCUIT #70 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #70 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #70 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 7 | #3 | [5 empty] | Three Phase | ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 X 0.866 ) = 0.5 VD |  | 2: Voltage Drop %; 3: ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD
[67 empty] | 72 | 0 | 0 | ENTER CIRCUIT #72 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #72 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #72 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 8 | #2 | [5 empty] | Voltage Drop L1 & L3 | ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 ) = 0.6 VD |  | 2: Voltage Drop % L1 & L3; 3: ( 0.6 VD ÷ 240 V X 100 ) = 0.3 % VD
[67 empty] | 74 | 0 | 0 | ENTER CIRCUIT #74 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #74 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #74 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 9 | #1 | [5 empty] | Voltage Drop L2 ( Hi-Leg ) | ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 X 0.866 ) = 0.5 VD |  | 2: Voltage Drop % L2 ( Hi-Leg ); 3: ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD
[67 empty] | 76 | 0 | 0 | ENTER CIRCUIT #76 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #76 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #76 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 10 | #1/0
[67 empty] | 78 | 0 | 0 | ENTER CIRCUIT #78 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #78 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #78 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 11 | #2/0
[67 empty] | 80 | 0 | 0 | ENTER CIRCUIT #80 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #80 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #80 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 12 | #3/0
[67 empty] | 82 | 0 | 0 | ENTER CIRCUIT #82 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #82 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #82 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 13 | #4/0
[67 empty] | 84 | 0 | 0 | ENTER CIRCUIT #84 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #84 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #84 NEUTRAL IDENTIFIER ( N or SPACE ) | [35 empty] | 14 | #250
[66 empty] | 0 |  | 0 |  |  | 0 |  |  | 0 | [37 empty] | 15 | #300
[112 empty] | 16 | #350
[112 empty] | 17 | #400
[68 empty] | AC/AL | [43 empty] | 18 | #500
ERROR
CHECK
[67 empty] | CU/AL? | AL
[67 empty] | AM72-CA | 0
[67 empty] | THHN-CA | 0
[67 empty] | XHHW-CA | 0
0

## Sec Cable (hidden)
[7 empty] | SHORT | WIRE | WIRE | GROUND | MAX |  |  |  | 3-COND W/GND SER CABLE AL
[7 empty] | C VALUE | RES | SIZE | SIZE | AMPS | [14 empty] | AMPACITY TABLE
AMPS | 57.9 | 0 | SER 3C AL | SER CABLE | 3-#4 AL | 1-#6 GND | 2353 | 0.508 | #4 | #6 | 65 | 4-4-4-6 | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
WIRE TEMP | 75 | 0 | SER 3C CU | SER CABLE | 3-#6 CU | 1-#6 GND | 2433 | 0.491 | #6 | #6 | 65 | 6-6-6-6 | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
# OF CONDUCTORS | 4 | 0 | SER 4C AL | SER CABLE | 4-#4 AL | 1-#6 GND | 2353 | 0.508 | #4 | #6 | 65 | 4-4-4-4-6 | [5 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
CU OR AL | AL | 0 | ROMEX 3C CU | ROMEX | 3-#6 CU | 1-#10 GND | 2433 | 0.491 | #6 | #10 | 65 | 6-6-6-6 |  |  |  | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
FEEDER TYPE | CONDUIT | 0 | MC 3C AL | MC CABLE | 3-#4 AL | 1-#6 GND | 2353 | 0.508 | #4 | #6 | 65 | 4-4-4-6 |  |  |  | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
|  | 0 | MC 4C AL | MC CABLE | 4-#4 AL | 1-#6 GND | 2353 | 0.508 | #4 | #6 | 65 | 4-4-4-4-6 |  |  |  | 102 | 65 | 2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3740 | 0.319 | #2 | 75 | 90 | 100
|  | 0 | MC 3C CU | MC CABLE | 3-#4 CU | 1-#8 GND | 3830 | 0.308 | #4 | #8 | 85 | 4-4-4-8 |  |  |  | 103 | 90 | 1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 | #1 | 85 | 100 | 115
|  | 0 | MC 4C CU | MC CABLE | 4-#4 CU | 1-#8 GND | 3830 | 0.308 | #4 | #8 | 85 | 4-4-4-4-8 |  |  |  | 104 | 100 | 1/0-1/0-1/0-2 | #1/0 | #2 | 120 | 10 | 104 | 5876 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-1 | #2/0 | #1 | 135 | 11 | 105 | 7373 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 155 | 12 | 106 | 9243 | 0.126 | #3/0 | 130 | 155 | 175
|  |  | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR |  |  |  | 107 | 155 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 180 | 13 | 107 | 11409 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | EXCEED | EXCEED | EXCEED | 180 | EXCEED | 108 | EXCEED | EXCEED
|  |  | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR | ERROR
[16 empty] | 101 |  | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 3- | #4 | AL |  |  | 3-#4 AL
|  |  | THE DESIGN LOAD OF | 57.9 | AMPS EXCEEDS THE MAXIMUM |  |  |  | THE DESIGN LOAD OF 57.9 AMPS EXCEEDS THE MAXIMUM | [8 empty] | 1- | #6 | GND |  |  | 1-#6 GND
|  |  | CABLE RATING OF | ERROR | AMPS |  |  |  | CABLE RATING OF ERROR AMPS
3-COND W/GND SER CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | CU | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 65 | 5 | 100 | 2433 | 0.491 | #6 | 55 | 65 | 75
[16 empty] | 101 | 65 | 4-4-4-6 | #4 | #6 | 85 | 6 | 101 | 3838 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 102 | 85 | 3-3-3-5 | #3 | #5 | 100 | 7 | 102 | 4833 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 103 | 100 | 2-2-2-4 | #2 | #4 | 115 | 8 | 103 | 6087 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 104 | 115 | 1-1-1-3 | #1 | #3 | 130 | 9 | 104 | 7579 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 105 | 130 | 1/0-1/0-1/0-2 | #1/0 | #2 | 150 | 10 | 105 | 9473 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 106 | 150 | 2/0-2/0-2/0-1 | #2/0 | #1 | 175 | 11 | 106 | 11703 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 107 | 175 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 200 | 12 | 107 | 14410 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 108 | 200 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 230 | 13 | 108 | 17483 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 109 | 230 | EXCEED | EXCEED | EXCEED | 230 | EXCEED | 109 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6 | #6 | #6 | 65 | 5 | 100 | 2433 | 0.491
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 3- | #6 | CU |  |  | 3-#6 CU
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
4-COND W/GND SER CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3740 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 90 | 1-1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 100 | 1/0-1/0-1/0-1/0-2 | #1/0 | #2 | 120 | 10 | 104 | 5876 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-2/0-1 | #2/0 | #1 | 135 | 11 | 105 | 7373 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 155 | 12 | 106 | 9243 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 155 | 4/0-4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 180 | 13 | 107 | 11409 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | 250-250-250-250-3/0 | #250 | #3/0 | 205 | 14 | 108 | 13236 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 205 | 300-300-300-300-4/0 | #300 | #4/0 | 230 | 15 | 109 | 15495 | 0.0707 | #300 | 190 | 230 | 255
[16 empty] | 110 | 230 | EXCEED | EXCEED | EXCEED | 230 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 101 |  | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 4- | #4 | AL |  |  | 4-#4 AL
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
3-COND W/GND ROMEX CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #10 | 65 | 5 | 100 | 2433 | 0.491 | #6 | 55 | 65 | 75
[16 empty] | 101 | 65 | 4-4-4-4 | #4 | #8 | 85 | 6 | 101 | 3838 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 102 | 85 | 2-2-2-2 | #2 | #8 | 115 | 7 | 102 | 4833 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 115 | EXCEED | EXCEED | EXCEED | 115 | EXCEED | 103 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6 | #6 | #10 | 65 | 5 | 100 | 2433 | 0.491
[18 empty] | ROMEX |  |  |  |  | ROMEX
[18 empty] | 3- | #6 | CU |  |  | 3-#6 CU
[18 empty] | 1- | #10 | GND |  |  | 1-#10 GND
3-COND W/GND MC CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 65 | 2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3734 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 90 | 1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 100 | 1/0-1/0-1/0-4 | #1/0 | #4 | 120 | 10 | 104 | 5852 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-4 | #2/0 | #4 | 135 | 11 | 105 | 7327 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-4 | #3/0 | #4 | 155 | 12 | 106 | 9077 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 155 | 4/0-4/0-4/0-2 | #4/0 | #2 | 180 | 13 | 107 | 11185 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | 250-250-250-2 | #250 | #2 | 205 | 14 | 108 | 12797 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 205 | 350-350-350-1 | #300 | #1 | 250 | 16 | 109 | 16795 | 0.0605 | #350 | 210 | 250 | 280
[16 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 101 |  | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 3- | #4 | AL |  |  | 3-#4 AL
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
4-COND W/GND MC CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3734 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 90 | 1-1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 100 | 1/0-1/0-1/0-1/0-4 | #1/0 | #4 | 120 | 10 | 104 | 5852 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-2/0-4 | #2/0 | #4 | 135 | 11 | 105 | 7327 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 155 | 12 | 106 | 9077 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 155 | 4/0-4/0-4/0-4/0-2 | #4/0 | #2 | 180 | 13 | 107 | 11185 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | 250-250-250-250-1 | #250 | #1 | 205 | 14 | 108 | 12797 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 205 | 350-350-350-350-1/0 | #350 | #1/0 | 250 | 16 | 109 | 16795 | 0.0605 | #350 | 210 | 250 | 280
[16 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 101 |  | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 4- | #4 | AL |  |  | 4-#4 AL
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
3-COND W/GND MC CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 101 | 85 | 3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 102 | 100 | 2-2-2-6 | #2 | #6 | 115 | 8 | 102 | 5989 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 115 | 1-1-1-6 | #1 | #6 | 130 | 9 | 103 | 7454 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 104 | 130 | 1/0-1/0-1/0-6 | #1/0 | #6 | 150 | 10 | 104 | 9210 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 105 | 150 | 2/0-2/0-2/0-6 | #2/0 | #6 | 175 | 11 | 105 | 11245 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 106 | 175 | 3/0-3/0-3/0-4 | #3/0 | #4 | 200 | 12 | 106 | 13656 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 107 | 200 | 4/0-4/0-4/0-4 | #4/0 | #4 | 230 | 13 | 107 | 16392 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 108 | 230 | 250-250-250-4 | #250 | #4 | 255 | 14 | 108 | 18311 | 0.0515 | #250 | 215 | 255 | 290
[16 empty] | 109 | 255 | 350-350-350-3 | #350 | #3 | 310 | 16 | 109 | 22646 | 0.0367 | #350 | 260 | 310 | 350
[16 empty] | 110 | 310 | EXCEED | EXCEED | EXCEED | 310 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 3- | #4 | CU |  |  | 3-#4 CU
[18 empty] | 1- | #8 | GND |  |  | 1-#8 GND
4-COND W/GND MC CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 57.9 |  | ROW | LOOKUP | WIRE | WIRE | NEUTRAL | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 4-4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 101 | 85 | 3-3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 102 | 100 | 2-2-2-2-6 | #2 | #6 | 115 | 8 | 102 | 5989 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 115 | 1-1-1-1-6 | #1 | #6 | 130 | 9 | 103 | 7454 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 104 | 130 | 1/0-1/0-1/0-1/0-6 | #1/0 | #6 | 150 | 10 | 104 | 9210 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 105 | 150 | 2/0-2/0-2/0-2/0-6 | #2/0 | #6 | 175 | 11 | 105 | 11245 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 106 | 175 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 200 | 12 | 106 | 13656 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 107 | 200 | 4/0-4/0-4/0-4/0-4 | #4/0 | #4 | 230 | 13 | 107 | 16392 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 108 | 230 | 250-250-250-250-4 | #250 | #4 | 255 | 14 | 108 | 18311 | 0.0515 | #250 | 215 | 255 | 290
[16 empty] | 109 | 255 | 350-350-350-350-3 | #350 | #3 | 310 | 16 | 109 | 22646 | 0.0367 | #350 | 260 | 310 | 350
[16 empty] | 110 | 310 | EXCEED | EXCEED | EXCEED | 310 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 4-4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 4- | #4 | CU |  |  | 4-#4 CU
[18 empty] | 1- | #8 | GND |  |  | 1-#8 GND

## Schedule
PANEL |  | CP1 |  |  |  |  | FEEDER | [6 empty] | 0
FED FROM |  | MAIN PANEL |  |  |  |  | NUMBER OF CONDUITS |  |  |  | 1 |  |  | 0
# CIRCUITS |  |  |  |  | 84 |  | FEEDER CONDUIT |  |  |  | 1 1/4''
HI VOLTAGE |  |  |  |  | 240 |  | WIRE SIZE L1 |  |  |  | #4 |  |  | SUB PANEL
LOW VOLTAGE |  |  |  |  | 120 |  | WIRE SIZE L2 |  |  |  | #4 |  |  | 0 | 0
PHASE |  |  |  |  | 3Y |  | WIRE SIZE L3 |  |  |  | #4
DESIGN LOAD AMPS |  |  |  |  | 57.9 |  | WIRE SIZE NEUTRAL |  |  |  | #4 |  | L1 L3 | 60
NEUTRAL BUS |  |  |  |  | YES |  | WIRE SIZE GROUND |  |  |  | #8 |  | HI LEG | 0 |  | L1-L3
GROUND BUS |  |  |  |  | YES | [8 empty] | A |  | HIGH LEG | 60
AVAILABLE FAULT CURRENT AT THIS PANEL |  |  |  |  | 15,304 | [8 empty] | -3P
MAIN BREAKER SIZE AMPS |  |  |  |  | 60 | [8 empty] | 0A-3P
FUSE HI-LEG AT
0
A
FUSE HI-LEG AT 0A
# | BKR | CIRCUIT DESCRIPTION | H | I | VA |  | VA | I | H | CIRCUIT DESCRIPTION | BKR | #
1 |  |  |  | G | 6000 | L1 | 1100 | G |  | LIGHTS | 20A-1P | 2 |  | 1
3 |  |  |  | G | 6000 | L2 | 1100 | G |  | LIGHTS | 20A-1P | 4 |  | 1
5 |  |  |  | G |  | L3 | 1100 | G |  | LIGHTS | 20A-1P | 6 |  | 1
7 |  |  |  | G |  | L1 |  | G |  |  |  | 8 |  | 1
9 |  |  |  | G |  | L2 |  | G |  |  |  | 10 |  | 1
11 |  |  |  | G |  | L3 |  | G |  |  |  | 12 |  | 1
13 |  |  |  | G |  | L1 |  | G |  | PINK CELLS ARE |  | 14 |  | 1
15 |  |  |  | G |  | L2 |  | G |  | PROTECTED IN DEMO |  | 16 |  | 1
17 |  |  |  | G |  | L3 |  | G |  |  |  | 18 |  | 1
19 |  |  |  | G |  | L1 |  | G |  |  |  | 20 |  | 1
21 |  |  |  | G |  | L2 |  | G |  |  |  | 22 |  | 1
23 |  |  |  | G |  | L3 |  | G |  |  |  | 24 |  | 1
25 |  |  |  | G |  | L1 |  | G |  |  |  | 26 |  | 1
27 |  |  |  | G |  | L2 |  | G |  |  |  | 28 |  | 1
29 |  |  |  | G |  | L3 |  | G |  |  |  | 30 |  | 1
31 |  |  |  | G |  | L1 |  | G |  |  |  | 32 |  | 1
33 |  |  |  | G |  | L2 |  | G |  |  |  | 34 |  | 1
35 |  |  |  | G |  | L3 |  | G |  |  |  | 36 |  | 1
37 |  |  |  | G |  | L1 |  | G |  |  |  | 38 |  | 1
39 |  |  |  | G |  | L2 |  | G |  |  |  | 40 |  | 1
41 |  |  |  | G |  | L3 |  | G |  |  |  | 42 |  | 1
43 |  |  |  | G |  | L1 |  | G |  |  |  | 44 |  | 1
45 |  |  |  | G |  | L2 |  | G |  |  |  | 46 |  | 1
47 |  |  |  | G |  | L3 |  | G |  |  |  | 48 |  | 1
49 |  |  |  | G |  | L1 |  | G |  |  |  | 50 |  | 1
51 |  |  |  | G |  | L2 |  | G |  |  |  | 52 |  | 1
53 |  |  |  | G |  | L3 |  | G |  |  |  | 54 |  | 1
55 |  |  |  | G |  | L1 |  | G |  |  |  | 56 |  | 1
57 |  |  |  | G |  | L2 |  | G |  |  |  | 58 |  | 1
59 |  |  |  | G |  | L3 |  | G |  |  |  | 60 |  | 1
61 |  |  |  | G |  | L1 |  | G |  |  |  | 62 |  | 1
63 |  |  |  | G |  | L2 |  | G |  |  |  | 64 |  | 1
65 |  |  |  | G |  | L3 |  | G |  |  |  | 66 |  | 1
67 |  |  |  | G |  | L1 |  | G |  |  |  | 68 |  | 1
69 |  |  |  | G |  | L2 |  | G |  |  |  | 70 |  | 1
71 |  |  |  | G |  | L3 |  | G |  |  |  | 72 |  | 1
73 |  |  |  | G |  | L1 |  | G |  |  |  | 74 |  | 1
75 |  |  |  | G |  | L2 |  | G |  |  |  | 76 |  | 1
77 |  |  |  | G |  | L3 |  | G |  |  |  | 78 |  | 1
79 |  |  |  | G |  | L1 |  | G |  |  |  | 80 |  | 1
81 |  |  |  | G |  | L2 |  | G |  |  |  | 82 |  | 1
83 |  |  |  | G |  | L3 |  | G |  |  |  | 84 |  | 1

## Calcs
LOAD CALCULATIONS FOR "PANEL CP1" | [8 empty] | BASED ON THE 2008 NEC | [7 empty] | RECEPTACLE | L1 | L2 | L3 | TOTAL |  | RECEPTACLE | L1 | L2 | L3 | TOTAL |  | RECEPTACLE | L1 | L2 | L3 | TOTAL | [12 empty] | 3Y
BASED ON THE 2008 NEC | [11 empty] | SUB PANEL PHASE | 1 |  |  | THIS PANEL | DIVERSITY | 0 | 0 |  | 0 |  | DIVERSITY | 0 |  | 0 | 0 |  | DIVERSITY | 0 | 0 | 0 | 0 | [12 empty] | 0 |  | 0
|  |  | L1 |  | L2 |  | L3 |  |  |  |  | SUB PANEL ERROR | 0 |  |  | SUB PANEL | DIVERSITY | 0 | 0 |  | 0 |  |  | 10000 |  | 10000 |  |  |  | 10000 | 10000 | 10000 |  |  | RECEPTACLE LOAD DIVERSITY | [7 empty] | L1 |  |  | L2 |  |  | L3
CALCULATED LOAD ( NEC 215.5 ) |  |  | 7100 | VA | 7100 | VA | 1100 | VA |  | 1100 | [7 empty] | 0 | 0 |  | 0 | [18 empty] | CALCULATED LOAD ( NEC 215.5 ) |  |  | 7100 |  |  | 7100 |  |  | 1100 | 3Y | NEUTRAL LOAD
[11 empty] | 0 | 0 | [5 empty] | 10000 | 10000 |  |  |  | 3-PHASE DELTA | #DIV/0! |  | #DIV/0! | #DIV/0! |  | 3-PHASE Y | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | L1 | L2 | L3 |  | THIS PANEL |  |  | 7100 |  |  | 7100 |  |  | 1100 |  | L1 | L2 | L3
CALCULATED LOAD WITH DEMAND FACTORS ( NEC 215.5 ) | [11 empty] | PHASE | 3Y |  |  |  | 1-PHASE | #DIV/0! | #DIV/0! |  | #DIV/0! |  |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | 1-PHASE |  |  |  |  | SUB PANEL |  |  | 0 |  |  | 0 |  |  |  | THIS PANEL | 0 | 0 | 0 | 0
| GENERAL LOAD |  | 7100 | VA | 7100 | VA | 1100 | VA |  |  |  | HI VOTLS | 240 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  | FIRST 10,000 W | 0 |  | 0 | 0 |  | FIRST 10,000 W | 0 | 0 | 0 | 0 | 3Y | 3-PHASE DELTA |  |  |  |  | TOTAL LOAD |  |  | 15300 | [6 empty] | SUB PANEL
| RECEPTACLE LOAD (NEC 220.14) | [10 empty] | LOW VOTLS | 120 |  |  |  | FIRST 10,000 W | 0 | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0 | 3Y | 3-PHASE Y | 0 | 0 | 0
|  | 1ST 10,000W | 0 | VA | 0 | VA | 0 | VA |  |  |  | KITCHEN LOADS | 0 | [7 empty] | 0 | [18 empty] | CALCULATED LOAD WITH DEMAND FACTORS ( NEC 215.5 ) | [9 empty] | SUM | 0 | 0 | 0
[12 empty] | NEUTRAL SIZE | FULL
| CONTINUOUS LOAD (NEC 215.2) |  | 0 | VA | 0 | VA | 0 | VA |  |  |  | HI-LEG SIZE | CONDUIT |  |  |  | KITCHEN | 1 | 1 | [9 empty] | OUTPUT |  |  |  |  | SUB PANEL |  | 0 | 0 |  |  |  | GENERAL LOAD |  | 7100 |  |  | 7100 |  |  | 1100 | MAX | 0
|  | PLUS 25% | 0 | VA | 0 | VA | 0 | VA |  |  |  | HAS SUB PANEL | NONE |  |  |  | LOADS | 2 | 1 | [9 empty] | GENERAL LOAD | 7100 | 7100 | 1100 | [8 empty] | THIS PANEL |  | 7100 |  |  | 7100 |  |  | 1100
| MOTOR LOAD (NEC 430.24) |  | 0 | VA | 0 | VA | 0 | VA |  |  |  | VD CALCS | YES |  |  |  |  | 3 | 0.9 | [9 empty] | RECEPTACLE LOAD | 0 | 0 | 0 | [8 empty] | SUB PANEL |  | 0 |  |  | 0 |  |  |  | AMPS | 0
|  | PLUS 25% OF LARGEST MOTOR | 0 | VA | 0 | VA | 0 | VA |  |  |  | FAULT METHOD | YES |  |  |  |  | 4 | 0.8 | [9 empty] | CONTINUOUS LOAD | 0 | 0 | 0
| KITCHEN LOAD (NEC 220.56) | [10 empty] | SOURCE | 3Y |  |  |  |  | 5 | 0.7 | [9 empty] | MOTOR LOAD | 0 | 0 | 0 | [18 empty] | 0
|  | L1 ( 0 X 1 ) = | 0 | VA | [7 empty] | PHASE | [5 empty] | 6 | 0.65 | [9 empty] | KITCHEN LOADS | 0 | 0 | 0 | [18 empty] | CP1
|  | L2 ( 0 X 1 ) = |  |  | 0 | VA | [10 empty] | 1 | [23 empty] | CONTINUOUS LOAD (NEC 215.2) |  | 0 |  |  | 0 |  |  | 0 |  | TRANSFORMER (3-PHASE)
|  | L3 ( 0 X 1 ) = |  |  |  |  | 0 | VA | [20 empty] | TOTALS | 7100 | 7100 | 1100 | [8 empty] | THIS PANEL |  | 0 |  |  | 0 |  |  | 0 |  | TRANSFORMER (1-PHASE)
TOTAL BALANCED LOAD (3-PHASE) |  |  | 1100 | VA | 1100 | VA | 1100 | VA | [8 empty] | L1 ( | 0 | 0 | X | 1 | ) = | L1 ( 0 X 1 ) = | [17 empty] | SUB PANEL |  | 0 |  |  | 0
TOTAL BALANCED LOAD (1-PHASE) |  |  | 6000 | VA | 6000 | VA | 0 | VA |  |  |  | L1 | 7100 | 6000 |  |  | L2 ( | 0 | 0 | X | 1 | ) = | L2 ( 0 X 1 ) =
TOTAL UNBALANCED LOAD (1-PHASE) |  |  | 0 | VA | 0 | VA | 0 | VA |  |  |  | L2 | 7100 | 6000 |  |  | L3 ( | 0 | 0 | X | 1 | ) = | L3 ( 0 X 1 ) =
[12 empty] | L3 | 1100 | [27 empty] | MOTOR LOAD (NEC 430.24) |  | 0 |  |  | 0 |  |  | 0
LINE AMPS BALANCED (3-PHASE) |  |  | 7.9 | A | 7.9 | A | 7.9 | A |  |  |  | 15300 | 15300 | 6000 | [26 empty] | THIS PANEL |  | 0 |  |  | 0 |  |  | 0
LINE AMPS BALANCED (1-PHASE) |  |  | 50 | A | 50 | A | 0 | A |  |  |  | 3-PHASE DELTA |  | 2 | 0 | [25 empty] | SUB PANEL |  | 0 |  |  | 0
LINE AMPS UNBALANCED (1-PHASE) |  |  | 0 | A | 0 | A | 0 | A |  |  |  | LOAD ERROR
| TOTALS |  | 57.9 | A | 57.9 | A | 7.9 | A |  |  |  | 0 | [10 empty] | 2000 | 3750 |  | 2500 |  | 2000 | [5 empty] | TOTALS |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 240 | 1.732 | 0 | 0
| ADJUSTMENT FACTOR |  | 0 | A | 0 | A | 0 | A | [25 empty] | PERCENT |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  | MAX MOTOR LOAD |  | 0 |  |  | 0 |  |  | 0
TOTAL DESIGN LOAD |  |  | 57.9 | A | 57.9 | A | 7.9 | A | [15 empty] | 2000 |  | 2000 |  | 2000 | [7 empty] | 10000 | 10000 | 10000 |  |  | THIS PANEL |  | 0 |  |  | 0 |  |  | 0
[12 empty] | NEUTRAL AMPS | 0 | [27 empty] | SUB PANEL |  | 0 |  |  | 0 |  |  | 0
VOLTAGE DROP CALCULATIONS | [11 empty] | NEUTRAL LOAD | 0 | [10 empty] | 1750 |  | 500 |  | 0 | [5 empty] | OUTPUT
|  | Three Phase | ( 2 X 10' L X 0.5080 R X 57.9 A ÷ 1,000 X 0.866 ) = 0.5 VD | [30 empty] | 1ST 10,00 VA |  | 0 | 0 | 0 | 0
|  | Voltage Drop % | ( 0.5 VD ÷ 240 V X 100 ) = 0.2 % VD | [8 empty] | 1-PHASE | 0 | [20 empty] | REMAINDER AT 50% |  |  |  |  | 0 |  | KITCHEN LOAD |  | 0 |  |  | 0 |  |  | 0
[12 empty] | AMPS | 0 | [27 empty] | THIS PANEL |  | 0 |  |  | 0 |  |  | 0
[41 empty] | SUB PANEL |  | 0 |  |  | 0 |  |  | 0
[12 empty] | 3-PHASE DELTA | 0
HARMONIC CURRENT CALCULATION ( NEC 310.15 B (4) C ) | [11 empty] | AMPS | 0
| ( Harmonic Load 0 VA ÷ Connected Load 15,300 VA ) X 100 = 0 % | [39 empty] | # OF KITCHEN LOADS |  | 0
| Harmonic Load Does Not Exceed 50% | [10 empty] | 3-PHASE Y | 0 | [27 empty] | THIS PANEL |  | 0
[12 empty] | AMPS | 0 | [27 empty] | SUB PANEL |  | 0
FAULT CURRENT CALCULATIONS
Available Fault Current at Starting Point (( 28,875 AFC X 1.00 UA ) + 0 MC ) = 28,875 AFC
|  | Conductor Factor CF - Formula ( 1.732 X 10 L X 28,875 AFC ) ÷ ( 2,346 C X 1 N X 240 V ) = 0.888 CF | [9 empty] | MAX LINE AMPS | 57.9 | [27 empty] | HARMONIC LOAD |  | 0
|  | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 0.888 CF ) = 0.530 CM | [38 empty] | THIS PANEL |  | 0
|  | Conductor Let-Through Current CLC - Formula ( 28,875 AFC X 0.530 CM ) = 15,304 CLC | [9 empty] | L1 | 7157.9 | [27 empty] | SUB PANEL |  | 0
[12 empty] | L2 | 1100
| A - Amps | [10 empty] | L3 | 1107.9
| AFC - Available Fault Current | [10 empty] | MAX WATTS | 7157.9 | [27 empty] | CP1
| C - Conductor Constant | [39 empty] | TRANSFORMER (3-PHASE)
| CF - Conductor Factor | [39 empty] | TRANSFORMER (1-PHASE)
| CLC - Conductor Let-Through Current | [10 empty] | HARMONIC LOAD | 0
| CM - Conductor Multiplier | [10 empty] | TOTAL LOAD | 15300 | [28 empty] | 1
| L - Length of Conductor | [10 empty] | HARMONIC % | 0
MC - Motor Contribution
| N - Number of Conductors Per Phase | [11 empty] | ( | Harmonic Load | 0 | VA ÷ | Connected Load | 15,300 | VA ) X 100 = | 0 | % | ( Harmonic Load 0 VA ÷ Connected Load 15,300 VA ) X 100 = 0 % | [19 empty] | 0
| R - Resistance | [9 empty] | YES
| UA - Utility Adjustment 1.1 | [9 empty] | YES | 0
| V - Voltage | [10 empty] | 0
| VA - Volt Amps | [10 empty] | 0
| VD - Voltage Drop | [10 empty] | 5
Prepared With Residential 1-Line 2014 Software - Copyright Durand & Associates
[12 empty] | 5 |  | 2 | 3 | 4 | 5
[12 empty] | A - Amps |  | A - Amps | A - Amps | A - Amps | A - Amps
[12 empty] | AFC - Available Fault Current |  | VA - Volt Amps | L - Length of Conductor | AFC - Available Fault Current | AFC - Available Fault Current
[12 empty] | C - Conductor Constant |  |  | R - Resistance | C - Conductor Constant | C - Conductor Constant
[12 empty] | CF - Conductor Factor |  |  | V - Voltage | CF - Conductor Factor | CF - Conductor Factor
[12 empty] | CLC - Conductor Let-Through Current |  |  | VA - Volt Amps | CLC - Conductor Let-Through Current | CLC - Conductor Let-Through Current
[12 empty] | CM - Conductor Multiplier |  |  | VD - Voltage Drop | CM - Conductor Multiplier | CM - Conductor Multiplier
[12 empty] | L - Length of Conductor |  |  |  | L - Length of Conductor | L - Length of Conductor
[12 empty] | MC - Motor Contribution |  |  |  | MC - Motor Contribution | MC - Motor Contribution
[12 empty] | N - Number of Conductors Per Phase |  |  |  | N - Number of Conductors Per Phase | N - Number of Conductors Per Phase
[12 empty] | R - Resistance |  |  |  | UA - Utility Adjustment 1.1 | R - Resistance
[12 empty] | UA - Utility Adjustment 1.1 |  |  |  | V - Voltage | UA - Utility Adjustment 1.1
[12 empty] | V - Voltage |  |  |  | VA - Volt Amps | V - Voltage
[12 empty] | VA - Volt Amps |  |  |  |  | VA - Volt Amps
[12 empty] | VD - Voltage Drop |  |  |  |  | VD - Voltage Drop
aaaa

## Short (hidden)
NO TRANSFORMER 3-PHASE Y
|  | Available Fault Current at Starting Point |  |  | (( | 28875 | AFC x | 1 | UA ) + | 0 | MC ) = | 28875 | AFC
|  | Available Fault Current at Starting Point |  |  | (( | 28,875 | AFC X | 1.00 | UA ) + | 0 | MC ) = | 28,875 | AFC |  |  |  | Available Fault Current at Starting Point (( 28,875 AFC X 1.00 UA ) + 0 MC ) = 28,875 AFC
28,875 AFC
Start > | < 28,875 AFC |  |  |  | < | 28,875 | AFC
[8 empty] | 0 | [5 empty] | 0.75 | 3/4"
| < 10' ' LENGTH |  |  |  | < | 10 | ' | LENGTH | [5 empty] | 1 | 1" | [8 empty] | CONDUIT
| - 0 0 | [5 empty] | - | 0 |  | 0 |  |  |  | 1.25 | 1 1/4"
| 15,304 - 1 1/4'' #4 #4 |  |  |  |  | 15,304 | - | 1 1/4'' |  | #4 |  | #4 |  | 1.5 | 1 1/2" | [7 empty] | GENERAL | 0
| 1 - #4 GROUND |  |  |  |  | 1 | - | #4 | GROUND |  |  |  |  | 2 | 2" | [7 empty] | RIGID | 1
[14 empty] | 2.5 | 2 1/2" | [7 empty] | EMT | 0
[14 empty] | 3 | 3" | [7 empty] | IMC | 0
[14 empty] | 3.5 | 3 1/2" | [7 empty] | PVC-40 | 0
End > | < 15,304 AFC |  |  |  | < | 15,304 | AFC | [6 empty] | 4 | 4" | [7 empty] | RIGID/PVC | 0
[23 empty] | FLEX | 0
[23 empty] | LT-FLEX | 0
| Step 4 - Conductor Factor CF - Formula | [21 empty] | STELL=1 PLASTIC=2 | 1
| Three Phase | [21 empty] | CU=1 AL=2 | 2
Conductor Factor CF - Formula | ( | 1.732 | x | 10 | L x | 28875 | AFC ) ÷ ( | 2346 | C x | 1 | N x | 240 | V ) = | 0.888 |  | CF | Print
Conductor Factor CF - Formula | ( | 1.732 | X | 10 | L X | 28,875 | AFC ) ÷ ( | 2,346 | C X | 1 | N X | 240 | V ) = | 0.888 |  | CF | Conductor Factor CF - Formula ( 1.732 X 10 L X 28,875 AFC ) ÷ ( 2,346 C X 1 N X 240 V ) = 0.888 CF | [5 empty] | TOTAL | 3
Step 5 - Conductor Multiplier CM - Formula
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.888 | CF ) = | 0.53 | CM | [7 empty] | Print
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 0.888 | CF ) = | 0.530 | CM | [7 empty] | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 0.888 CF ) = 0.530 CM
3
Step 6 - Conductor Let-Through Current CLC - Formula
Conductor Let-Through Current CLC - Formula | ( | 28875 | AFC X | 0.53 | CM ) = | 15303.75 | CLC | [9 empty] | Print | [5 empty] | 3 |  | 1 | 2 | 3 | 4 | 5 | 6
Conductor Let-Through Current CLC - Formula | ( | 28,875 | AFC X | 0.530 | CM ) = | 15,304 | CLC |  |  | 15,304 CLC | [6 empty] | Conductor Let-Through Current CLC - Formula ( 28,875 AFC X 0.530 CM ) = 15,304 CLC | [5 empty] | Steel Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit | SER-ROMEX | SER-ROMEX
[23 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | CABLE | CABLE
|  |  | Conductor Let-Through Current CLC - Formula ( 28,875 AFC X 0.530 CM ) = 15,304 CLC | [15 empty] | C7 | #4 | 6 |  | Cables AL |  | Cables CU | Cables CU | Cables AL | Cables AL | CU | AL
[18 empty] | #4 |  |  |  | 1 | 237 | #14 | 389 | 389 | 237 | 237 | 389 | 237
[18 empty] | ERROR |  |  |  | 2 | 376 | #12 | 617 | 617 | 376 | 376 | 617 | 376
[22 empty] | 3 | 599 | #10 | 981 | 982 | 599 | 599 | 982 | 599
[22 empty] | 4 | 951 | #8 | 1557 | 1559 | 951 | 952 | 1560 | 952
[22 empty] | 5 | 1481 | #6 | 2425 | 2430 | 1481 | 1482 | 2433 | 1482
[22 empty] | 6 | 2346 | #4 | 3806 | 3826 | 2346 | 2350 | 3838 | 2353
[22 empty] | 7 | 2952 | #3 | 4774 | 4811 | 2952 | 2961 | 4833 | 2966
[22 empty] | 8 | 3713 | #2 | 5907 | 6044 | 3713 | 3730 | 6087 | 3740
[21 empty] | 6 | 9 | 4645 | #1 | 7293 | 7493 | 4645 | 4678 | 7579 | 4699
[22 empty] | 10 | 5777 | #1/0 | 8925 | 9317 | 5777 | 5838 | 9473 | 5876
[22 empty] | 11 | 7187 | #2/0 | 10755 | 11424 | 7187 | 7301 | 11703 | 7373
[22 empty] | 12 | 8826 | #3/0 | 12844 | 13923 | 8826 | 9110 | 14410 | 9243
[22 empty] | 13 | 10741 | #4/0 | 15082 | 16673 | 10741 | 11174 | 17438 | 11409
[22 empty] | 14 | 12122 | #250 | 16483 | 18594 | 12122 | 12862 | 19779 | 13236
[22 empty] | 15 | 13910 | #300 | 18177 | 20868 | 13910 | 14923 | 22525 | 15495
[22 empty] | 16 | 15484 | #350 | 19704 | 22737 | 15484 | 16813 | 24904 | 17635
[22 empty] | 17 | 16671 | #400 | 20566 | 24297 | 16671 | 18506 | 26916 | 19588
[22 empty] | 18 | 18756 | #500 | 22185 | 26706 | 18756 | 21391 | 30096 | 23018
[22 empty] | 2346 | #4

## Output-Input (hidden)
OUTPUT
|  | PANEL | FED FROM | NUMBER OF | HIGH | LOW | PHASE | HIGH LEG | NEUTRAL | GROUND | GROUND | WIRE | WIRE | WIRE | WIRE | CONDUIT | MINIMUM | KITCHEN | % FACTOR | MAIN | MAIN BKR | L2 | AFC | AFC AT | UTILITY | AFC AT | NUMBER | CONDUIT | CONDUIT | WIRE | WIRE | WIRE | WIRE | WIRE | WIRE | NEUTRAL | NEUTRAL | GROUND | GROUND | 1-PHASE | 1-PHASE | 3-PHASE Y | 3-PHASE Y | 3-PHASE D | 3-PHASE D | 3-PHASE D | 3-PHASE D | GENERAL | GENERAL | GENERAL | RECEPTACLE | RECEPTACLE | RECEPTACLE | CONTINUOUS | CONTINUOUS | CONTINUOUS | MOTOR | MOTOR | MOTOR | LARGEST | LARGEST | LARGEST | KITCHEN | KITCHEN | KITCHEN | MAX
|  | NAME |  | CIRCUITS | VOLTAGE | VOLTAGE |  | SIZE | SIZE | BUS | WIRE | TYPE | CA/AL | TEMP | LENGTH | TYPE | AMPS | LOADS |  | BREAKER | SIZE | FUSE | CALC | START | VOLTAGE | THIS | OF | SIZE | SIZE | SIZE | CODE | SIZE | CODE | SIZE | CODE | SIZE | CODE | SIZE | WIRE | L1 & L3 | L1 & L3 | L1 L2 L3 | L1 L2 L3 | L2 | L2 | L1 & L3 | L1 & L3 | LOAD | LOAD | LOAD | LOADS | LOADS | LOADS | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | MOTOR | MOTOR | MOTOR | LOAD | LOAD | LOAD | AMPS
|  | TEXT | VALUE | VALUE | [5 empty] | Y/N | Y/N | [8 empty] | Y/N |  |  | METHOD | POINT | ADJUST | PANEL | CONDUITS |  | CODE | L1 | L1 | L2 | L2 | L3 | L3 |  |  |  | CODE | VD | % VD | VD | % VD | VD | % VD | VD | % VD | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3
|  | CP1 | MAIN PANEL | 84 | 240 | 120 | 3Y | CONDUIT | FULL | 0 | Y | THHN | AL | 75 | 10 | RIGID | 0 | 0 | 0 | Y | 60 | 0 | 0 | 28875 | 1 | 15.3 | 1 | 1 1/4'' | 1.25 | #4 | 6 | #4 | 6 | #4 | 6 | #4 | 6 | #8 | 4 | 0.6 VD | 0.3 % VD | 0.5 VD | 0.2 % VD | 0.5 VD | 0.2 % VD | 0.6 VD | 0.3 % VD | 7100 | 7100 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.9
'
|  | CP1 | [12 empty] | 10'
A-
|  | IMPUT | [5 empty] | BACK TO | THIS | CHECK | [10 empty] | 3
|  | AFC |  |  |  |  | MSWBD | MSWBD | PANEL | [11 empty] | P
|  | AT MIAN |  |  |  | HI VOLT | [5 empty] | SOURCE VOLTAGE IS | 0 | V | SOURCE VOLTAGE IS 0V
|  | 28875 | 28875 | [17 empty] | 60A-3P
[6 empty] | L VOLT | [5 empty] | SOURCE VOLTAGE IS | 0 | V | SOURCE VOLTAGE IS 0V
CONDUIT
| 3Y |  |  |  |  | PHASE | 3Y | 3Y |  |  |  | SOURCE PHASE IS | 3Y |  | SOURCE PHASE IS 3Y
| 3-POLE | MAIN BKR | L2
|  | AMPS | FUSE |  |  | CALC | 28875 | 28875
| NUMBER | 60 | 0
|  | A | A |  |  | FAULT | NO | NO
| TEXT | 60A
[6 empty] | VD | NO | NO
|  | # OF CONDUITS | 1
-
|  | CONDUIT SIZE | 1 1/4''
SPACE
|  | CONDUIT TYPE | RIGID
1-1 1/4'' RIGID
CABLE
|  | WIRE 1 | 4-#4 THHN AL |  | ERROR |  | 4-#4 THHN AL
|  | WIRE 2 | 1-#8 AL GND |  | ERROR |  | 1-#8 AL GND
WIRE 3
WIRE 4
| 0 | AFC AT PANEL | 15.3
K
15.3 K
VOLTAGE DROP
0.2 % VD
0.2 % VD
|  | CONDUIT LENGTH | 10
|  | PANEL | '
10'
NONE |  | CONDUIT LENGTH | 0
|  | PANEL - XMFR | '
|  | CONDUIT LENGTH | 50
|  | XMFR-SUBPANEL | '
|  | HARMONIC LOAD | 0
|  | PHASE | 3Y
|  | HI-LEG | CONDUIT

## Directory
CIRCUIT DIRECTORY PANEL |  |  | CP1 |  | 0
0
CIR | DESCRIPTION | L1 | DESCRIPTION | CIR
1 |  | L2 | LIGHTS | 2 | 1
3 |  | L3 | LIGHTS | 4 | 1
5 |  | L1 | LIGHTS | 6 | 1
7 |  | L2 |  | 8 | 1
9 |  | L3 |  | 10 | 1
11 |  | L1 |  | 12 | 1
13 |  | L2 | PINK CELLS ARE | 14 | 1
15 |  | L3 | PROTECTED IN DEMO | 16 | 1
17 |  | L1 |  | 18 | 1
19 |  | L2 |  | 20 | 1
21 |  | L3 |  | 22 | 1
23 |  | L1 |  | 24 | 1
25 |  | L2 |  | 26 | 1
27 |  | L3 |  | 28 | 1
29 |  | L1 |  | 30 | 1
31 |  | L2 |  | 32 | 1
33 |  | L3 |  | 34 | 1
35 |  | L1 |  | 36 | 1
37 |  | L2 |  | 38 | 1
39 |  | L3 |  | 40 | 1
41 |  | L1 |  | 42 | 1
43 |  | L2 |  | 44 | 1
45 |  | L3 |  | 46 | 1
47 |  | L1 |  | 48 | 1
49 |  | L2 |  | 50 | 1
51 |  | L3 |  | 52 | 1
53 |  | L1 |  | 54 | 1
55 |  | L2 |  | 56 | 1
57 |  | L3 |  | 58 | 1
59 |  | L1 |  | 60 | 1
61 |  | L2 |  | 62 | 1
63 |  | L3 |  | 64 | 1
65 |  | L1 |  | 66 | 1
67 |  | L2 |  | 68 | 1
69 |  | L3 |  | 70 | 1
71 |  | L1 |  | 72 | 1
73 |  | L2 |  | 74 | 1
75 |  | L3 |  | 76 | 1
77 |  | L1 |  | 78 | 1
79 |  | L2 |  | 80 | 1
81 |  | L3 |  | 82 | 1
83 |  | 0 |  | 84 | 1

## S-Input (hidden)
Residential 1-Line 2008 (Ver 8.0A) - Copyright Durand & Associates |  |  |  |  | Warning DO NOT use copy/paste commands with Panel | [8 empty] | LOAD CALCULATIONS FOR "PANEL | [62 empty] | # OF CONDUITS
[14 empty] | HP2 | [54 empty] | ERROR IN MAIN PANEL |  | 0 | [7 empty] | 3/4'' |  | EMT | ( | 4 | - | #6 |  |  | 1 | - | CONDUIT | 1 - CONDUIT | [40 empty] | PANEL VOLTAGE HI |  | 240 |  | SECONDARY | KVA | AMPS | [14 empty] | PRIMARY
SUB PANEL |  | HP2 | [9 empty] | Y |  | " | [62 empty] | CONDUITS | 3/4'' | EMT | [8 empty] | 3/4'' |  | EMT | 3/4'' EMT | [21 empty] | INPUT | EMT | [17 empty] | SUB PANEL VOLTAGE HI |  | 240 | [7 empty] | 0 | [10 empty] | INPUT | 0 |  | PRIMARY
FED FROM |  | CP1 |  | AUTO |  |  | THIS SUB PANEL IS NOT BEING USED |  |  |  | NONE | SIZE |  | LOAD CALCULATIONS FOR "PANEL HP2" | [48 empty] | #N/A |  |  | ERROR | [36 empty] | OVER CURRENT MODULE |  | PRIMARY | [7 empty] | 1. GENERAL | 0 |  | CONDUIT SIZING MODULE | [15 empty] | CP1 | [9 empty] | 0 | [10 empty] | 1. GENERAL | 0 |  | CONDUIT SIZING MODULE
# OF CIRCUITS |  |  |  | 84 |  | SOURCE | IF YOU WISH TO USE THIS SUB PANEL GO BACK |  |  |  | 0 | [54 empty] | CODE |  | CELL NAME | [5 empty] | USE 3-PHASE XMFR |  | 0 |  |  |  |  | WIRE SIZE MODULE (4" MAX CONDUIT) | [31 empty] | 2. RIGID | 0 | [38 empty] | 2. RIGID | 0
HI VOLTAGE |  |  |  | 240 |  | 240 | TO THE INPUT TAB A SELECT SUB PANEL BRK |  |  |  | 28875 | Y SIZE | [63 empty] | 0 |  |  | HI | NEUTRAL | CU/AL? | AL |  |  |  |  | WIRES |  | PRIMARY MIN |  | 0 | WIRES | [10 empty] | FUSE SIZING AMPS | 0 | 0 | [7 empty] | 3. EMT | 3 |  | CONDUIT TYPE | 3 | [35 empty] | 3. EMT | 0 |  | CONDUIT TYPE | 0
LOW VOLTAGE |  |  |  | 120 |  | 120 | AFC AT THIS PANEL |  | 2,892 | [55 empty] | 1 | 0 | 0 | ENTER NUMBER OF CIRCUITS | [5 empty] | CP1 |  |  |  |  | LEG | AMPS | WIRE TEMP | 75 | 0 | L2 AMPS |  | 0 | 1 | 0 | XMFR AMPS | 0 | [12 empty] | # OF PHASE WIRES | 1 | #N/A | [7 empty] | 4. IMC | 0 |  | WIRE AREA SQ IN | 0.1887 | [18 empty] | OUTPUT | 0 | 0 | [14 empty] | 4. IMC | 0 |  | WIRE AREA SQ IN | #N/A
PHASE |  |  |  | 1 |  | NONE |  |  |  |  | 0 | [53 empty] | 2 | 0 | 0 | ERROR IN MAIN PANEL | SOURCE VOTAGE IS | 240 | SOURCE VOTAGE IS 240 | [5 empty] | DESIGN AMPS | 0 | 0 |  | DESIGN AMPS (NDA) | 0 |  | NEUTRAL AMPS |  | 0 | 1 | 0 |  | 0 | [22 empty] | 5. PVC-40 | 0 |  | PERCENT FILL | 0.4 | [35 empty] | 5. PVC-40 | 0 |  | PERCENT FILL | 0.31
FEEDER TYPE |  |  |  | SER |  |  | FEEDER | [57 empty] | 3 | 0 | 0 | ERROR IN MAIN PANEL | SOURCE VOTAGE IS | 120 | SOURCE VOTAGE IS 120 |  |  | TRANSFORMER (1-PHASE) |  | 0 |  | 0 | 0 | 0 | LOOKUP AMPS | 0 |  | 33% OF PHASE |  | 16.7 | 1 | 16.7 |  | 0 | [22 empty] | 6. RIGID/PVC | 0 | [21 empty] | PRIMARY | [16 empty] | 6. RIGID/PVC | 0
[7 empty] | NUMBER OF CABLES |  | 1 | [55 empty] | 4 | 0 | 0 | CHECK ENTRY | 0 | 0 | 0 |  |  | TRANSFORMER (3-PHASE) |  | 1 |  |  | 0 | 0 | NET Y/N | Y | 4 | MAX |  |  |  | 16.7 | [14 empty] | LOOKUP | FUSE/BKR | [8 empty] | 7. FLEX | 0 |  | LOOKUP | 40% | CONDUIT | EMT | CONDUIT |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | [5 empty] | OUTPUT | 0 | 0 | [14 empty] | 7. FLEX | 0 |  | LOOKUP | 31% | CONDUIT | EMT | CONDUIT |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
[7 empty] | FEEDER CABLE |  | SER CABLE | [5 empty] | CP1 | [49 empty] | 5 | 0 | 0 | ENTER NEUTRAL SIZE |  |  | 0 |  |  |  |  | 0 | CONNECTED LOAD | 0 |  | 0 | HAR Y/N | N | 0 | [19 empty] | GROUND | AMP | [8 empty] | 8. LT-FLEX | 0 |  | TABLE | FILL | SIZE | AREA | SIZE |  | SIZE | GENERAL | RIGID | EMT | IMC | PVC-40 | RIGID/PVC | FLEX | LT-FLEX | [5 empty] | PRIMARY WIRE LOOKUP | [16 empty] | 8. LT-FLEX | 0 |  | TABLE | FILL | SIZE | AREA | SIZE |  | SIZE | GENERAL | RIGID | EMT | IMC | PVC-40 | RIGID/PVC | FLEX | LT-FLEX
[7 empty] | WIRE SIZE L1 |  | #6 | [5 empty] | TRANSFORMER (1-PHASE) | [49 empty] | 6 | 0 | 0 | ENTER MINIMUM NET AMPS |  | MASTER | [6 empty] | 50% CONNECTED | 0 |  |  | SUBTOTAL |  | 4 | [19 empty] | AMPS | RATING | [8 empty] | OUTPUT | 3 |  |  |  |  | SQ IN |  |  |  | AREA | AREA | AREA | AREA | AREA | AREA | AREA | AREA | [22 empty] | OUTPUT | 0 |  |  |  |  | SQ IN |  |  |  | AREA | AREA | AREA | AREA | AREA | AREA | AREA | AREA
|  |  |  | Y |  |  | WIRE SIZE L2 |  | #6 |  |  | KKK |  |  | TRANSFORMER (3-PHASE) | [49 empty] | 7 | 0 | 0 | ENTER GROUND WIRE Y/N |  | ERROR |  |  |  | CP1 |  |  | HARMONIC LOAD | 0 | [24 empty] | 0 | 60 | [11 empty] | 0 | 0.1216 | 0.5 | 0.304 | 0.5 |  |  | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | [25 empty] | 0 | 0.09424 | 0.5 | 0.304 | 0.5 |  |  | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN
|  |  |  | THHN | [7 empty] | KKK | [50 empty] | 84 |  | 8 | 0 | 0 | ENTER WIRE TYPE |  | 0 |  |  |  | CP1 |  |  |  | N |  |  |  | PRIMARY | [10 empty] | PRIMARY | [9 empty] | 60 | 70 | [11 empty] | 0.1216 | 0.2132 | 0.75 | 0.533 | 0.75 |  | 0.5 | 0.285 | 0.314 | 0.304 | 0.342 | 0.285 | 0.304 | 0.317 | 0.314 | [25 empty] | 0.09424 | 0.16523 | 0.75 | 0.533 | 0.75 |  | 0.5 | 0.285 | 0.314 | 0.304 | 0.342 | 0.285 | 0.304 | 0.317 | 0.314
WIRE CU/AL? |  |  |  | AL |  |  | WIRE SIZE NEUTRAL |  | #6 | [5 empty] | 0 | 4 | [48 empty] | 9 | 0 | 0 | ENTER WIRE CU/AL | [12 empty] | LOOKUP | LOOKUP | SELECTED | ADJUST | SELECTED | WIRE | WIRE | WIRE | 60º C | 75 C | 90º C |  | 60º C | 75 C | 90º C | AMPACITY TABLE | [6 empty] | 70 | 80 | [11 empty] | 0.2132 | 0.3456 | 1 | 0.864 | 1 |  | 0.75 | 0.508 | 0.549 | 0.533 | 0.586 | 0.508 | 0.533 | 0.533 | 0.541 |  | SINGLE PHASE TRANSFORMERS |  |  |  | THREE PHASE TRANSFORMERS | [19 empty] | 0.16523 | 0.26784 | 1 | 0.864 | 1 |  | 0.75 | 0.508 | 0.549 | 0.533 | 0.586 | 0.508 | 0.533 | 0.533 | 0.541
WIRE TEMP ºC |  |  |  | 75 |  |  | WIRE SIZE GROUND |  | #6 | [5 empty] | NONE | [49 empty] | 10 | 0 | 0 | ENTER WIRE TEMP | [12 empty] | WIRE | WIRE | WIRE | WIRE | WIRE | SIZE | SIZE | PER | AMPS | AMPS | AMPS |  | AMPS | AMPS | AMPS | WIRE | 60º C | 75 C | 90º C | 60º C | 75 C | 90º C | 80 | 90 | [11 empty] | 0.3456 | 0.5984 | 1.25 | 1.496 | 1.25 |  | 1 | 0.817 | 0.888 | 0.864 | 0.959 | 0.832 | 0.864 | 0.817 | 0.872 |  |  | KVA | AMPS |  |  | KVA | AMPS |  | TRANSFORMER | [15 empty] | 0.26784 | 0.46376 | 1.25 | 1.496 | 1.25 |  | 1 | 0.817 | 0.888 | 0.864 | 0.959 | 0.832 | 0.864 | 0.817 | 0.872
WIRE LENGTH |  |  |  | 50 | [60 empty] | 11 | 0 | 0 | ENTER WIRE LENGTH | [12 empty] | AMPS | AMPS | AMPS | AMPS | AMPS | AWG | CODE | PHASE | AL | AL | AL |  | ERR | ERR | ERR | SIZE | AMPS | AMPS | AMPS | AMPS | AMPS | AMPS | 90 | 100 | [11 empty] | 0.5984 | 0.8144 | 1.5 | 2.036 | 1.5 |  | 1.25 | 1.277 | 1.526 | 1.496 | 1.646 | 1.453 | 1.495 | 1.277 | 1.528 | 0 | 0 | 15 | 63 | 0 | 0 | 25 | 60 |  | MENU | [15 empty] | 0.46376 | 0.63116 | 1.5 | 2.036 | 1.5 |  | 1.25 | 1.277 | 1.526 | 1.496 | 1.646 | 1.453 | 1.495 | 1.277 | 1.528
|  |  |  | EMT | [60 empty] | 12 | 0 | 0 | ENTER CONDUIT TYPE | 1 | 0 | [10 empty] | 0 | 0 | ERR | 50 | 50 | #6 | 5 | 1 | 40 | 50 | 60 |  | ERR | ERR | ERR | AWG | CU | CU | CU | AL | AL | AL | 100 | 110 | [11 empty] | 0.8144 | 1.3424 | 2 | 3.356 | 2 |  | 1.5 | 1.857 | 2.071 | 2.036 | 2.223 | 1.986 | 2.036 | 1.857 | 1.979 | 63 | 15 | 20 | 83 | 60 | 25 | 30 | 72 | [16 empty] | #N/A | 0.63116 | 1.0404 | 2 | 3.356 | 2 |  | 1.5 | 1.857 | 2.071 | 2.036 | 2.223 | 1.986 | 2.036 | 1.857 | 1.979
MINIMUM AMPS |  |  |  | 0 | [60 empty] | 13 | 0 | 0 | CHECK ENTRY | [12 empty] | 50 | #VALUE! | ERR | 65 | 65 | #4 | 6 | 1 | 55 | 65 | 75 |  | ERR | ERR | ERR | #6 | 55 | 65 | 75 | 40 | 50 | 60 | 110 | 125 | [11 empty] | 1.3424 | 2.3432 | 2.5 | 5.858 | 2.5 |  | 2 | 3.245 | 3.408 | 3.356 | 3.629 | 3.291 | 3.355 | 3.269 | 3.245 | 83 | 20 | 25 | 104 | 72 | 30 | 37.5 | 90 | [16 empty] | #N/A | 1.0404 | 1.816 | 2.5 | 5.858 | 2.5 |  | 2 | 3.245 | 3.408 | 3.356 | 3.629 | 3.291 | 3.355 | 3.269 | 3.245
[8 empty] | DEMO VERSION | [56 empty] | 14 | 0 | 0 | ENTER MIN AMPS (L2) | [12 empty] | 65 | #VALUE! | ERR | 75 | 75 | #4 | 6 | 1 | 65 | 75 | 85 |  | ERR | ERR | ERR | #4 | 70 | 85 | 95 | 55 | 65 | 75 | 125 | 150 | [11 empty] | 2.3432 | 3.5384 | 3 | 8.846 | 3 |  | 2.5 | 4.695 | 4.866 | 5.858 | 5.135 | 4.695 | 4.788 | 4.909 | 4.879 | 104 | 25 | 30 | 125 | 90 | 37.5 | 45 | 108 |  |  | AUTO | 1 | [12 empty] | #N/A | 1.816 | 2.7423 | 3 | 8.846 | 3 |  | 2.5 | 4.695 | 4.866 | 5.858 | 5.135 | 4.695 | 4.788 | 4.909 | 4.879
# KITCHEN LOADS |  |  |  | 0 | [60 empty] | 15 | 0 | 0 | ENTER # OF KITCHEN LOADS | 0 | 0 |  |  |  | MATCH | 99 | [5 empty] | 75 | #VALUE! | ERR | 90 | 90 | #2 | 8 | 1 | 75 | 90 | 100 |  | ERR | ERR | ERR | #3 | 85 | 100 | 110 | 65 | 75 | 85 | 150 | 175 | [11 empty] | 3.5384 | 4.618 | 3.5 | 11.545 | 3.5 |  | 3 | 7.069 | 7.499 | 8.846 | 7.922 | 7.268 | 7.393 | 7.069 | 7.475 | 125 | 30 | 37.5 | 156 | 108 | 45 | 50 | 120 |  |  | AUTO | 1 | [12 empty] | #N/A | 2.7423 | 3.5789 | 3.5 | 11.545 | 3.5 |  | 3 | 7.069 | 7.499 | 8.846 | 7.922 | 7.268 | 7.393 | 7.069 | 7.475
% FACTOR |  |  |  | 0 | [60 empty] | 16 | 0 | 0 | ENTER % FACTOR | [12 empty] | 90 | #VALUE! | ERR | 100 | 100 | #1 | 9 | 1 | 85 | 100 | 115 |  | ERR | ERR | ERR | #2 | 95 | 115 | 130 | 75 | 90 | 100 | 175 | 200 | [11 empty] | 4.618 | 5.9012 | 4 | 14.753 | 4 |  | 3.5 | 9.621 | 10.01 | 11.545 | 10.584 | 9.737 | 9.866 | 9.621 | 9.731 | 156 | 37.5 | 50 | 208 | 120 | 50 | 60 | 144 |  |  | AUTO | 1 | [13 empty] | 3.579 | 4.5734 | 4 | 14.753 | 4 |  | 3.5 | 9.621 | 10.01 | 11.545 | 10.584 | 9.737 | 9.866 | 9.621 | 9.731
[65 empty] | 17 | 0 | 0 | ENTER VD % FACTOR | [12 empty] | 100 | #VALUE! | ERR | 120 | 120 | #1/0 | 10 | 1 | 100 | 120 | 135 |  | ERR | ERR | ERR | #1 | 110 | 130 | 150 | 85 | 100 | 115 | 200 | 225 | [17 empty] | 4 | 12.554 | 12.833 | 14.753 | 13.631 | 12.554 | 12.73 | 12.566 | 12.692 | 208 | 50 | 75 | 313 | 144 | 60 | 75 | 180 |  |  | AUTO | 1 | [19 empty] | 4 | 12.554 | 12.833 | 14.753 | 13.631 | 12.554 | 12.73 | 12.566 | 12.692
MAIN BKR Y/N |  |  |  | Y | [44 empty] | DELTA | DELTA | DELTA | DELTA | 1-PHASE | 1-PHASE | 1-PHASE | 1-PHASE | 3-PHASE | 3-PHASE | 3-PHASE | 3-PHASE | 3-PHASE | 3-PHASE |  |  | 18 | 0 | 0 | ENTER MAIN BKR Y/N | [5 empty] | XMFR | 0 | [5 empty] | 120 | #VALUE! | ERR | 135 | 135 | #2/0 | 11 | 1 | 115 | 135 | 150 |  | ERR | ERR | ERR | #1/0 | 125 | 150 | 170 | 100 | 120 | 135 | 225 | 250 | [11 empty] | CONDUIT SIZE | 0.75 | DIFFERENT SIZE WIRES | [12 empty] | 313 | 75 | 100 | 400 | 180 | 75 | 100 | 241 |  |  | AUTO | 1 | [13 empty] | CONDUIT SIZE | #N/A | DIFFERENT SIZE WIRES
BREAKER SIZE |  |  |  | 60 | [7 empty] | ACTIVE | PHASE | CONNECTED | CONNECTED | CONNECTED | GENERAL | GENERAL | GENERAL | GENERAL | GENERAL | GENERAL | DIVERSITY | DIVERSITY | DIVERSITY | DIVERSITY | DIVERSITY | DIVERSITY | CONTINUOUS | CONTINUOUS | CONTINUOUS | CONTINUOUS | CONTINUOUS | CONTINUOUS | HARMONIC | HARMONIC | MOTOR | MOTOR | MOTOR | MOTOR | MOTOR | MOTOR | KITCHEN | KITCHEN | KITCHEN | KITCHEN | KITCHEN | KITCHEN | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL | NEUTRAL |  |  | 19 | 0 | 0 | USE AL ON "-CA" WIRE |  | SOURCE POWER IS 3D |  |  |  |  | 0 | [5 empty] | 135 | #VALUE! | ERR | 155 | 155 | #3/0 | 12 | 1 | 130 | 155 | 175 |  | ERR | ERR | ERR | #2/0 | 145 | 175 | 195 | 115 | 135 | 150 | 250 | 300 | [11 empty] | CONDUIT TYPE | EMT | [13 empty] | 400 | 75 | 100 | 400 | 241 | 100 | 112.5 | 271 |  |  | AUTO | 1 | [13 empty] | CONDUIT TYPE | EMT
|  |  |  | 0 | [60 empty] | 20 | 0 | 0 | LOAD EXCEEDS 400 AMPS |  | SOURCE POWER IS 3Y |  |  |  |  | 0 | [5 empty] | 155 | #VALUE! | ERR | 180 | 180 | #4/0 | 13 | 1 | 150 | 180 | 205 |  | ERR | ERR | ERR | #3/0 | 165 | 200 | 225 | 130 | 155 | 175 | 300 | 350 | [11 empty] | CONDUIT SIZE | NOT USED | SAME SIZE WIRES | [12 empty] | 400 | 75 | 100 | 400 | 271 | 112.5 | 150 | 361 |  |  | AUTO | 1 | [13 empty] | CONDUIT SIZE | #N/A | SAME SIZE WIRES
[12 empty] | CIRCUIT | LEG | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD |  |  | 21 | 0 | 0 | ENTER CALCULATION METHOD > > |  | SOURCE POWER IS 1-PHASE | [10 empty] | 180 | #VALUE! | ERR | 205 | 205 | #250 | 14 | 1 | 170 | 205 | 230 |  | ERR | ERR | ERR | #4/0 | 195 | 230 | 260 | 150 | 180 | 205 | 350 | 400 | [11 empty] | CONDUIT SIZE | 0.75 | DIFFERENT SIZE WIRES | [22 empty] | AUTO | 1 | [13 empty] | CONDUIT SIZE | #N/A | #N/A
# | BKR | CIRCUIT DESCRIPTION | I | VA |  | VA | I | CIRCUIT DESCRIPTION | BKR | # |  |  |  | L1 | L2 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | ODD CIR | EVEN CIR | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L2 | L2 | L3 | L3 | L1 | L1 | L3 | L3 | L1 | L1 | L2 | L2 | L1 | L1 | L2 | L2 | L3 | L3 |  |  | 22 | 0 | 0 | ENTER AFC AT STARTING POINT |  | 0 | [10 empty] | 205 | #VALUE! | ERR | 230 | 230 | #300 | 15 | 1 | 190 | 230 | 255 |  | ERR | ERR | ERR | #250 | 215 | 255 | 290 | 170 | 205 | 230 | 400 | 450 | [11 empty] | # OF WIRES | 4 | [23 empty] | AUTO | 1 | [13 empty] | # OF WIRES | 2
1 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 2 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 23 | 0 | 0 | ENTER UTILITY VOLTAGE ADJUSTMENT | [6 empty] | 0 | [5 empty] | 230 | #VALUE! | ERR | 250 | 250 | #350 | 16 | 1 | 210 | 250 | 280 |  | ERR | ERR | ERR | #300 | 240 | 285 | 320 | 190 | 230 | 255 | 450 | 500 | [28 empty] | 1-PHASE | 1-PHASE |  | 3-PHASE | 3-PHASE |  |  |  | AUTO | 1
3 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 4 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 24 | 0 | 0 | ENTER SOURCE PHASE |  | XMFR POWER IS 3-PHASE Y | [7 empty] | CONDUIT SIZE | 0.75 |  | 250 | #VALUE! | ERR | 270 | 270 | #400 | 17 | 1 | 225 | 270 | 305 |  | ERR | ERR | ERR | #350 | 260 | 310 | 350 | 210 | 250 | 280 | 500 | 600 | [19 empty] | EMT | CONDUIT | [7 empty] | KVA | AMPS |  | KVA | AMPS |  |  |  | AUTO | 1 | [21 empty] | EMT | CONDUIT
5 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 6 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 25 | 0 | 0 | DELTA LOAD ERROR |  | XMFR POWER IS 1-PHASE | [8 empty] | 3/4'' |  | 270 | #VALUE! | ERR | 310 | 310 | #500 | 18 | 1 | 260 | 310 | 350 |  | ERR | ERR | ERR | #400 | 280 | 335 | 380 | 225 | 270 | 305 | 600 | 700 | [14 empty] | 2-WIRE | 3-WIRE | 4-WIRE |  |  | AREA | SIZE | [5 empty] | SELECTED KVA | 0 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | [16 empty] | 2-WIRE | 3-WIRE | 4-WIRE |  |  | AREA | SIZE
7 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 8 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 26 | 0 | 0 | ENTER PANEL NAME | [10 empty] | 0 |  | 310 | #VALUE! | #VALUE! | 360 | 360 | #4/0 | 13 | 2 | [7 empty] | #500 | 320 | 380 | 430 | 260 | 310 | 350 | 700 | 800 | [19 empty] | SQ IN | [6 empty] | MIN AMPS XMFR | 0 | 0 | 0 |  | 0 | 0 | [26 empty] | SQ IN
9 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 10 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 27 | 0 | 0 | ENTER SOURCE | [10 empty] | 3/4'' |  | 360 | #VALUE! | #VALUE! | 410 | 410 | #250 | 14 | 2 | [14 empty] | 800 | 1000 | [11 empty] | 1 | 0 | 0 | 2 | 0 | 0 | 2.3984 | 0.0507 | 0.1216 | 0.5 | [5 empty] | DESIGN AMPS XMFR | 0 | 0 | 0 |  | 0 | 0 | [18 empty] | 1 | 1 | 2 | 2 | 0 | 0 | 1.8588 | 0.0507 | 0.09424 | 0.5
11 |  | PINK CELLS ARE | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 12 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 28 | 0 | 0 | ERROR > |  | 0 | [10 empty] | 410 | #VALUE! | #VALUE! | 460 | 460 | #300 | 15 | 2 | [14 empty] | 1000 | 1200 | [11 empty] | 2 | 2 | 4 | 0 | 3 | 4 | 4.2051 | 0.0507 | 0.2132 | 0.75 | [5 empty] | MIN AMPS | 0 |  | 0 |  |  | 0 | [18 empty] | 2 | 0 | 0 | 0 | 3 | 0 | 3.259 | 0.0507 | 0.16523 | 0.75
13 |  | PROTECTED IN DEMO | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 14 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 29 | 0 | 0 | ENTER GROUND WIRE Y/N | [12 empty] | 460 | #VALUE! | #VALUE! | 500 | 500 | #350 | 16 | 2 | [22 empty] | L1 | L2 | L3 |  |  | 3 | 0 | 0 | 0 | 0 | 0 | 6.8166 | 0.0507 | 0.3456 | 1 | [5 empty] | DESIGN AMPS | 0 |  | 0 |  |  | 0 | [18 empty] | 3 | 0 | 0 | 0 | 0 | 4 | 5.2828 | 0.0507 | 0.26784 | 1
15 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 16 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 30 | 0 | 0 | ENTER WIRE TYPE |  | 0 |  |  |  | 1 | [6 empty] | 500 | #VALUE! | #VALUE! | 540 | 540 | #400 | 17 | 2 | [27 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 11.8028 | 0.0507 | 0.5984 | 1.25 | [5 empty] | MAX |  | 0 | 0 |  | 0 | 0 | [18 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 9.1471 | 0.0507 | 0.46376 | 1.25
17 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 18 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 31 | 0 | 0 | ENTER WIRE CU/AL |  | SOURCE FEED IS 1-PHASE |  |  |  | NONE | [6 empty] | 540 | #VALUE! | #VALUE! | 620 | 620 | #500 | 18 | 2 | [14 empty] | UNDER 800A | 60 | 60 |  | 0 | 60 |  | AMP | 60 | 60 |  |  |  | 5 | 0 | 0 | 0 | 0 | 0 | 16.0631 | 0.0507 | 0.8144 | 1.5 | [30 empty] | 5 | 0 | 0 | 0 | 0 | 0 | 12.4489 | 0.0507 | 0.63116 | 1.5
19 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 20 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 32 | 0 | 0 | USE AL ON "-CA" WIRE | [12 empty] | WIRE AMPS: 620; WIRE AMPS: 690; WIRE AMPS: 690; SIZE AWG: #300; SIZE CODE: 15; PER PHASE: 3 | [11 empty] | OVER 800A |  | 60 | [5 empty] | A-2P | A-3P |  |  |  | 6 | 0 | 0 | 0 | 0 | 0 | 26.4773 | 0.0507 | 1.3424 | 2 | [30 empty] | 6 | 0 | 0 | 0 | 0 | 0 | 20.5199 | 0.0507 | 1.0404 | 2
21 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 22 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 33 | 0 | 0 | ENTER WIRE TEMP | [12 empty] | WIRE AMPS: 690; WIRE AMPS: 750; WIRE AMPS: 750; SIZE AWG: #350; SIZE CODE: 16; PER PHASE: 3 | [9 empty] | AMP | 60 | RATING | 60 |  |  | H8 | 1 |  | SPACE | [5 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 46.217 | 0.0507 | 2.3432 | 2.5 | [30 empty] | 7 | 0 | 0 | 0 | 0 | 0 | 35.8181 | 0.0507 | 1.816 | 2.5
23 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 24 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 34 | 0 | 0 | ENTER WIRE LENGTH | [12 empty] | WIRE AMPS: 750; WIRE AMPS: 810; WIRE AMPS: 810; SIZE AWG: #400; SIZE CODE: 17; PER PHASE: 3 | [9 empty] | SPACE | A | HI LEG FUSE | 0 | 60 |  | H10 | 0 | [7 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 69.7909 | 0.0507 | 3.5384 | 3 | [8 empty] | 1=PHASE | 0 | [20 empty] | 8 | 0 | 0 | 0 | 0 | 0 | 54.088 | 0.0507 | 2.7423 | 3
25 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 26 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 35 | 0 | 0 | ENTER CONDUIT TYPE | [12 empty] | WIRE AMPS: 810; WIRE AMPS: 930; WIRE AMPS: 930; SIZE AWG: #500; SIZE CODE: 18; PER PHASE: 3 | [24 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 91.0848 | 0.0507 | 4.618 | 3.5 | [8 empty] | 3-PHASE | [21 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 70.5907 | 0.0507 | 3.5789 | 3.5
27 |  |  | G |  | L2 |  | G |  |  | 28 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 36 | 0 | 0 | ENTER TRANSFORMER % Z RATING | [12 empty] | WIRE AMPS: 930; WIRE AMPS: 1000; WIRE AMPS: 1000; SIZE AWG: #350; SIZE CODE: 16; PER PHASE: 4 | [24 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 116.3945 | 0.0507 | 5.9012 | 4 | [17 empty] | PRIMARY | [12 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 90.2057 | 0.0507 | 4.5734 | 4
29 |  |  | G |  | L1 |  | G |  |  | 30 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 37 | 0 | 0 | SHOW VD CALCS | [12 empty] | WIRE AMPS: 1000; WIRE AMPS: 1080; WIRE AMPS: 1080; SIZE AWG: #400; SIZE CODE: 17; PER PHASE: 4 | [11 empty] | WIRE FILL SIZING MODULE | [27 empty] | Primary voltage | [11 empty] | WIRE FILL SIZING MODULE
31 |  |  | G |  | L2 |  | G |  |  | 32 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [7 empty] | 0 | [14 empty] | WIRE AMPS: 1080; WIRE AMPS: 1240; WIRE AMPS: 1240; SIZE AWG: #500; SIZE CODE: 18; PER PHASE: 4 | [12 empty] | L1 | [12 empty] | 2 | [5 empty] | L2 RESISTANCE CALCULATION | [20 empty] | L1 | [12 empty] | 1
33 |  |  | G |  | L1 |  | G |  |  | 34 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [20 empty] | WIRE AMPS: 1240; WIRE AMPS: 1250; WIRE AMPS: 1250; SIZE AWG: #350; SIZE CODE: 16; PER PHASE: 5 | [11 empty] | WIRE CODE (NPHC) | 5 | [12 empty] | 0.75 | [14 empty] | SINGLE PHASE TRANSFORMERS |  |  |  | THREE PHASE TRANSFORMERS | [6 empty] | WIRE CODE (NPHC) | #N/A | [12 empty] | 0.5
35 |  |  | G |  | L2 |  | G |  |  | 36 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 1 | 0 | 0 | ENTER CIRCUIT #1 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #1 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #1 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: 1250; WIRE AMPS: 1350; WIRE AMPS: 1350; SIZE AWG: #400; SIZE CODE: 17; PER PHASE: 5 | [11 empty] | WIRE TYPE (NWTYP) | THHN | [6 empty] | 60A-2P | X X X | [10 empty] | 1 | 1 | / | 0.808 | = | 0 |  |  |  |  | KVA | AMPS |  |  | KVA | AMPS |  |  |  |  | WIRE TYPE (NWTYP) | 0 | [14 empty] | 1-PHASE | 3-PHASE
37 |  |  | G |  | L1 |  | G |  |  | 38 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 3 | 0 | 0 | ENTER CIRCUIT #3 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #3 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #3 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: 1350; WIRE AMPS: 1550; WIRE AMPS: 1550; SIZE AWG: #500; SIZE CODE: 18; PER PHASE: 5 | [11 empty] | CU/AL ? | AL | [18 empty] | 2 | 1 | / | 0.808 | = | 0 |  |  | 0 | 0 | 15 | 63 | 0 | 0 | 25 | 60 |  |  |  |  | CU/AL ? | 0 | [12 empty] | 208 VOLT LOAD AMPS |  | 0 | 0
39 |  |  | G |  | L2 |  | G |  |  | 40 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 5 | 0 | 0 | ENTER CIRCUIT #5 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #5 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #5 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: 1550; WIRE AMPS: 1620; WIRE AMPS: 1620; SIZE AWG: #400; SIZE CODE: 17; PER PHASE: 6 | [11 empty] | GND WIRE CODE | 4 | [18 empty] | 3 | 1 | / | 0.808 | = | 0 |  |  | 63 | 15 | 20 | 83 | 60 | 25 | 30 | 72 |  |  |  |  | GND WIRE CODE | 4 | [12 empty] | SECONDARY VOLTS |  | 240 | 240
41 |  |  | G |  | L1 |  | G |  |  | 42 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 7 | 0 | 0 | ENTER CIRCUIT #7 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #7 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #7 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: 1620; WIRE AMPS: 1860; WIRE AMPS: 1860; SIZE AWG: #500; SIZE CODE: 18; PER PHASE: 6 | [11 empty] | NEUTRAL Y/N | Y | 0 | [17 empty] | 4 | 1 | / | 0.808 | = | 0 |  |  | 83 | 20 | 25 | 104 | 72 | 30 | 37.5 | 90 |  |  |  |  | NEUTRAL Y/N | N | 0 | [11 empty] | VA |  | 0 | 0
43 |  |  | G |  | L2 |  | G |  |  | 44 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 9 | 0 | 0 | ENTER CIRCUIT #9 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #9 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #9 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT | [11 empty] | #OF WIRE | 2 | 2 | [17 empty] | 5 | 1 | / | 0.808 | = | 0 |  |  | 104 | 25 | 30 | 125 | 90 | 37.5 | 45 | 108 |  |  |  |  | #OF WIRE | 2 | 2 | [11 empty] | PRIMARY VOLTS |  | 240 | 240
45 |  |  | G |  | L1 |  | G |  |  | 46 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 11 | 0 | 0 | ENTER CIRCUIT #11 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #11 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #11 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: SELECTED; WIRE AMPS: WIRE; WIRE AMPS: WIRE; WIRE AMPS: WIRE | [11 empty] | TOTAL WIRES |  | 2 | [17 empty] | 6 | 1 | / | 0.808 | = | 0 |  |  | 125 | 30 | 37.5 | 156 | 108 | 45 | 50 | 120 |  |  |  |  | TOTAL WIRES |  | 2 | [11 empty] | PRIMARY AMPS |  | 0 | 0
47 |  |  | G |  | L2 |  | G |  |  | 48 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 13 | 0 | 0 | ENTER CIRCUIT #13 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #13 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #13 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: WIRE; WIRE AMPS: SIZE; WIRE AMPS: SIZE; WIRE AMPS: PER | [11 empty] | GND WIRE CODE | [27 empty] | 156 | 37.5 | 50 | 208 | 120 | 50 | 60 | 144 |  |  |  |  | GND WIRE CODE
49 |  |  | G |  | L1 |  | G |  |  | 50 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 15 | 0 | 0 | ENTER CIRCUIT #15 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #15 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #15 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: AMPS; WIRE AMPS: AWG; WIRE AMPS: CODE; WIRE AMPS: PHASE | [24 empty] | VOLTAGE DROP MODULE |  |  |  |  | PRIMARY |  | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0 | 208 | 50 | 75 | 313 | 144 | 60 | 75 | 180 | [17 empty] | VOLTAGE DROP MODULE PRIMARY
51 |  |  | G |  | L2 |  | G |  |  | 52 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 17 | 0 | 0 | ENTER CIRCUIT #17 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #17 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #17 NEUTRAL IDENTIFIER ( N or SPACE ) | [5 empty] | L1-L3 | WIRE AMPS: 50; WIRE AMPS: #6; WIRE AMPS: 5; WIRE AMPS: 1; SIZE AWG: HI LEG | [11 empty] | WIRE | WIRE | ST |  | WIRE | WIRE | ST | ST | ST | ST | CA | CA | CA |  | 1-PHASE | 3Y | 3D | 3D | 1-PHASE | [9 empty] | 313 | 75 | 100 | 400 | 180 | 75 | 100 | 241 |  |  |  |  | WIRE | WIRE | ST |  | WIRE | WIRE | ST | ST | ST | ST | CA | CA | CA
53 |  |  | G |  | L1 |  | G |  |  | 54 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 19 | 0 | 0 | ENTER CIRCUIT #19 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #19 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #19 NEUTRAL IDENTIFIER ( N or SPACE ) | [5 empty] | L2 | 50 | #6 | 5 | 1 |  | 50 | #6 | 5 | [14 empty] | SIZE | SIZE | THHN |  | WIRE | WIRE | THW | RHW | THHN | XHHW | THW-CA | THHN-CA | XHHW-CA | CU/AL? | AL |  | HI LEG |  |  |  | SINGLE CONDUCTOR | [6 empty] | 0.808 | 400 | 75 | 100 | 400 | 241 | 100 | 112.5 | 271 |  |  |  |  | SIZE | SIZE | THHN |  | WIRE | WIRE | THW | RHW | THHN | XHHW | THW-CA | THHN-CA | XHHW-CA | CU/AL? | 0
55 |  |  | G |  | L2 |  | G |  |  | 56 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 21 | 0 | 0 | ENTER CIRCUIT #21 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #21 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #21 NEUTRAL IDENTIFIER ( N or SPACE ) | [5 empty] | NETURAL | 50 | #6 | 5 | 1 |  | 50 | #6 | 5 | [14 empty] | AWG | CODE | SIZE |  | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | ONE WAY DISTANCE | 50 | [13 empty] | 400 | 75 | 100 | 400 | 271 | 112.5 | 150 | 361 |  |  |  |  | AWG | CODE | SIZE |  | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | SIZE | ONE WAY DISTANCE | 0
57 |  |  | G |  | L1 |  | G |  |  | 58 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 23 | 0 | 0 | ENTER CIRCUIT #23 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #23 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #23 NEUTRAL IDENTIFIER ( N or SPACE ) | [5 empty] | PRIMARY | WIRE AMPS: 50; WIRE AMPS: #N/A; WIRE AMPS: #N/A; WIRE AMPS: #N/A | [13 empty] | SQ IN |  | AWG | CODE | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | TOTAL LOAD | 0 | 0 | 0 | 0 |  |  | CALCULATED RESISTANCE OF CONDUCTOR(S) | [6 empty] | 0.808 | [14 empty] | SQ IN |  | AWG | CODE | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | SQ IN | TOTAL LOAD | 0
59 |  |  | G |  | L2 |  | G |  |  | 60 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 25 | 0 | 0 | ENTER CIRCUIT #25 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #25 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #25 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | SIZE AWG: NEUTRAL | [11 empty] | #10 | 3 | 0.0211 |  | #10 | 3 | 0.0333 | 0.0333 | 0.0211 | 0.0243 | 0.051 | 0.051 | 0.0394 | VOLTAGE | 240 | [25 empty] | #10 | 3 | 0.0211 |  | #10 | 3 | 0.0333 | 0.0333 | 0.0211 | 0.0243 | 0.051 | 0.051 | 0.0394 | VOLTAGE | 240
61 |  |  | G |  | L1 |  | G |  |  | 62 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 27 | 0 | 0 | ENTER CIRCUIT #27 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #27 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #27 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: GROUND SIZE MODULE; SIZE AWG: 50; SIZE CODE: #6; PER PHASE: 5 | [11 empty] | #8 | 4 | 0.0366 |  | #8 | 4 | 0.0556 | 0.0556 | 0.0366 | 0.0437 | 0.051 | 0.051 | 0.0394 | # OF PHASE WIRES | 1 | [25 empty] | #8 | 4 | 0.0366 |  | #8 | 4 | 0.0556 | 0.0556 | 0.0366 | 0.0437 | 0.051 | 0.051 | 0.0394 | # OF PHASE WIRES | #N/A
63 |  |  | G |  | L2 |  | G |  |  | 64 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 29 | 0 | 0 | ENTER CIRCUIT #29 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #29 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #29 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: GND Y/N? (NGYN); WIRE AMPS: Y; SIZE AWG: 50; SIZE CODE: #6; PER PHASE: 5 | [11 empty] | #6 | 5 | 0.0507 |  | #6 | 5 | 0.0726 | 0.1041 | 0.0507 | 0.059 | 0.066 | 0.0452 | 0.0394 | WIRE CODE | 5 | 5 | 5 | 5 | [22 empty] | #6 | 5 | 0.0507 |  | #6 | 5 | 0.0726 | 0.1041 | 0.0507 | 0.059 | 0.066 | 0.0452 | 0.0394 | WIRE CODE | #N/A
65 |  |  | G |  | L1 |  | G |  |  | 66 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 31 | 0 | 0 | ENTER CIRCUIT #31 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #31 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #31 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: MAX AMPS (NMA); WIRE AMPS: 60 | [11 empty] | #4 | 6 | 0.0824 |  | #4 | 6 | 0.0973 | 0.1333 | 0.0824 | 0.0814 | 0.0881 | 0.073 | 0.053 | WIRE | WIRE | RES | RES | RES |  |  | L1 & L2 RESISTANCE CALCULATION | [19 empty] | #4 | 6 | 0.0824 |  | #4 | 6 | 0.0973 | 0.1333 | 0.0824 | 0.0814 | 0.0881 | 0.073 | 0.053 | WIRE | WIRE | RES | RES | RES |  |  | RESISTANCE CALCULATION
67 |  |  | G |  | L2 |  | G |  |  | 68 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 33 | 0 | 0 | ENTER CIRCUIT #33 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #33 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #33 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: CU/AL? (NCUAL2); WIRE AMPS: AL | [11 empty] | #3 | 7 | 0.0973 |  | #3 | 7 | 0.1134 | 0.1521 | 0.0973 | 0.0962 |  |  |  | SIZE | SIZE | NEC | NEC | NEC | [22 empty] | #3 | 7 | 0.0973 |  | #3 | 7 | 0.1134 | 0.1521 | 0.0973 | 0.0962 |  |  |  | SIZE | SIZE | NEC | NEC | NEC
69 |  |  | G |  | L1 |  | G |  |  | 70 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 35 | 0 | 0 | ENTER CIRCUIT #35 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #35 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #35 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: GND_TABLE | [11 empty] | #2 | 8 | 0.1158 |  | #2 | 8 | 0.1333 | 0.175 | 0.1158 | 0.1146 | 0.1194 | 0.1017 | 0.073 | AWG | CODE | AL | CU | AL |  |  | 1 | 1 | / | 0.808 | = | 0 | [14 empty] | #2 | 8 | 0.1158 |  | #2 | 8 | 0.1333 | 0.175 | 0.1158 | 0.1146 | 0.1194 | 0.1017 | 0.073 | AWG | CODE | AL | CU | AL |  |  | 1 | 1 | / | #N/A | = | #N/A
71 |  |  | G |  | L2 |  | G |  |  | 72 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 37 | 0 | 0 | ENTER CIRCUIT #37 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #37 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #37 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | LOOKUP |  | RATING | SEL | SEL |  | RATING | CU | CU | AL | AL | [11 empty] | #1 | 9 | 0.1562 |  | #1 | 9 | 0.1901 | 0.266 | 0.1562 | 0.1534 | 0.1698 | 0.1352 | 0.1017 | #6 | 5 | 0.808 | 0.491 | 0.808 |  |  | 2 | 1 | / | 0.808 | = | 0 | [14 empty] | #1 | 9 | 0.1562 |  | #1 | 9 | 0.1901 | 0.266 | 0.1562 | 0.1534 | 0.1698 | 0.1352 | 0.1017 | #6 | 5 | 0.808 | 0.491 | 0.808 |  |  | 2 | 1 | / | #N/A | = | #N/A
73 |  |  | G |  | L1 |  | G |  |  | 74 | 1 | 0 | L1 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | [6 empty] | 39 | 0 | 0 | ENTER CIRCUIT #39 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #39 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #39 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | GROUND |  | OVER | WIRE | WIRE |  | OVER | WIRE | WIRE | WIRE | WIRE | [11 empty] | #1/0 | 10 | 0.1855 |  | #1/0 | 10 | 0.2223 | 0.3039 | 0.1855 | 0.1825 | 0.1963 | 0.159 | 0.1352 | #4 | 6 | 0.508 | 0.308 | 0.508 |  |  | 3 | 1 | / | 0.808 | = | 0 |  |  |  | CONDUCTOR | [10 empty] | #1/0 | 10 | 0.1855 |  | #1/0 | 10 | 0.2223 | 0.3039 | 0.1855 | 0.1825 | 0.1963 | 0.159 | 0.1352 | #4 | 6 | 0.508 | 0.308 | 0.508 |  |  | 3 | 1 | / | #N/A | = | #N/A
75 |  |  | G |  | L2 |  | G |  |  | 76 | 1 | 0 | L2 |  | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | [8 empty] | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 41 | 0 | 0 | ENTER CIRCUIT #41 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #41 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #41 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | AMPS |  | CURRENT | SIZE | CODE |  | CURRENT | SIZE | CODE | SIZE | CODE | [11 empty] | #2/0 | 11 | 0.2223 |  | #2/0 | 11 | 0.2624 | 0.3505 | 0.2223 | 0.219 | 0.2332 | 0.1924 | 0.159 | #3 | 7 | 0.403 | 0.245 | 0.403 |  |  | 4 | 1 | / | 0.808 | = | 0 |  |  | SYSTEM GROUND | SIZE CODE | 5 |  | #8 | [7 empty] | #2/0 | 11 | 0.2223 |  | #2/0 | 11 | 0.2624 | 0.3505 | 0.2223 | 0.219 | 0.2332 | 0.1924 | 0.159 | #3 | 7 | 0.403 | 0.245 | 0.403 |  |  | 4 | 1 | / | #N/A | = | #N/A
77 |  |  | G |  | L1 |  | G |  |  | 78 | 1 | 0 | L1 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  | 43 | 0 | 0 | ENTER CIRCUIT #43 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #43 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #43 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 0 |  | 60 | #8 | 4 |  | 60 | #10 | 3 | #8 | 4 | [11 empty] | #3/0 | 12 | 0.2679 |  | #3/0 | 12 | 0.3117 | 0.4072 | 0.2679 | 0.2642 | 0.2733 | 0.229 | 0.1885 | #2 | 8 | 0.319 | 0.194 | 0.319 |  |  | 5 | 1 | / | 0.808 | = | 0 |  |  |  |  | #N/A |  | #N/A | [7 empty] | #3/0 | 12 | 0.2679 |  | #3/0 | 12 | 0.3117 | 0.4072 | 0.2679 | 0.2642 | 0.2733 | 0.229 | 0.1885 | #2 | 8 | 0.319 | 0.194 | 0.319 |  |  | 5 | 1 | / | #N/A | = | #N/A
79 |  |  | G |  | L2 |  | G |  |  | 80 | 1 | 0 | L2 | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | [6 empty] | 45 | 0 | 0 | ENTER CIRCUIT #45 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #45 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #45 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 60 |  | 100 | #6 | 5 |  | 100 | #8 | 4 | #6 | 5 | [11 empty] | #4/0 | 13 | 0.3237 |  | #4/0 | 13 | 0.3718 | 0.4754 | 0.3237 | 0.3197 | 0.3267 | 0.278 | 0.229 | #1 | 9 | 0.253 | 0.154 | 0.253 |  |  | 6 | 1 | / | 0.808 | = | 0 | [14 empty] | #4/0 | 13 | 0.3237 |  | #4/0 | 13 | 0.3718 | 0.4754 | 0.3237 | 0.3197 | 0.3267 | 0.278 | 0.229 | #1 | 9 | 0.253 | 0.154 | 0.253 |  |  | 6 | 1 | / | #N/A | = | #N/A
81 |  |  | G |  | L1 |  | G |  |  | 82 | 1 | 0 | L1 | 0 | 0 |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 47 | 0 | 0 | ENTER CIRCUIT #47 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #47 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #47 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 100 |  | 200 | #4 | 6 |  | 200 | #6 | 5 | #4 | 6 | [11 empty] | #250 | 14 | 0.397 |  | #250 | 14 | 0.4596 | 0.6291 | 0.397 | 0.3904 | 0.4128 | 0.3525 | 0.2733 | #1/0 | 10 | 0.201 | 0.122 | 0.201 | [11 empty] | WIRE | WIRE | SYS | [8 empty] | #250 | 14 | 0.397 |  | #250 | 14 | 0.4596 | 0.6291 | 0.397 | 0.3904 | 0.4128 | 0.3525 | 0.2733 | #1/0 | 10 | 0.201 | 0.122 | 0.201
83 |  |  | G |  | L2 |  | G |  |  | 84 | 1 | 0 | L2 |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 49 | 0 | 0 | ENTER CIRCUIT #49 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #49 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #49 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 200 |  | 300 | #2 | 8 |  | 300 | #4 | 6 | #2 | 8 | [11 empty] | #300 | 15 | 0.4608 |  | #300 | 15 | 0.5281 | 0.7088 | 0.4608 | 0.4536 | 0.4717 | 0.4071 | 0.3421 | #2/0 | 11 | 0.159 | 0.0967 | 0.159 |  |  | PARALLEL CONDUCTORS |  |  | 1 | / | 0 | = | 0 |  | SIZE | SIZE | GND | [8 empty] | #300 | 15 | 0.4608 |  | #300 | 15 | 0.5281 | 0.7088 | 0.4608 | 0.4536 | 0.4717 | 0.4071 | 0.3421 | #2/0 | 11 | 0.159 | 0.0967 | 0.159 |  |  | PARALLEL CONDUCTORS |  |  | 1 | / | #N/A | = | #N/A
[65 empty] | 51 | 0 | 0 | ENTER CIRCUIT #51 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #51 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #51 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 300 |  | 400 | #1 | 9 |  | 400 | #3 | 7 | #1 | 9 | [11 empty] | #350 | 16 | 0.5242 |  | #350 | 16 | 0.5958 | 0.787 | 0.5242 | 0.5166 | 0.5281 | 0.4656 | 0.4015 | #3/0 | 12 | 0.126 | 0.0766 | 0.126 | [11 empty] | CODE | AWG | SIZE | [8 empty] | #350 | 16 | 0.5242 |  | #350 | 16 | 0.5958 | 0.787 | 0.5242 | 0.5166 | 0.5281 | 0.4656 | 0.4015 | #3/0 | 12 | 0.126 | 0.0766 | 0.126
Residential 1-Line 2008 (Ver 8.0A) - Copyright Durand & Associates |  |  |  |  | Warning DO NOT use copy/paste commands with Panel | [32 empty] | MAX |  | MAX |  | MAX | [6 empty] | DELTA |  | DELTA |  | 1-PHASE |  | 1-PHASE |  | 3-PHASE |  | 3-PHASE |  | 3-PHASE |  |  |  | 53 | 0 | 0 | ENTER CIRCUIT #53 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #53 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #53 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 400 |  | 500 | #1/0 | 10 |  | 500 | #2 | 8 | #1/0 | 10 | [11 empty] | #400 | 17 | 0.5863 |  | #400 | 17 | 0.6619 | 0.8626 | 0.5863 | 0.5782 | 0.5876 | 0.5216 | 0.4536 | #4/0 | 13 | 0.1 | 0.0608 | 0.1 |  |  | SINGLE CONDUCTOR | [6 empty] | 0.808 |  | 5 | #6 | #8 | [8 empty] | #400 | 17 | 0.5863 |  | #400 | 17 | 0.6619 | 0.8626 | 0.5863 | 0.5782 | 0.5876 | 0.5216 | 0.4536 | #4/0 | 13 | 0.1 | 0.0608 | 0.1 |  |  | SINGLE CONDUCTOR | [6 empty] | #N/A
[14 empty] | CONNECTED | CONNECTED | CONNECTED |  | GENERAL |  | GENERAL |  | GENERAL |  | DIVERSITY |  | DIVERSITY |  | DIVERSITY |  | CONTINUOUS |  | CONTINUOUS |  | CONTINUOUS |  | TOTAL |  | MOTOR |  | MOTOR |  | MOTOR | KITCHEN |  | KITCHEN |  | KITCHEN |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  | NEUTRAL |  |  |  | 55 | 0 | 0 | ENTER CIRCUIT #55 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #55 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #55 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 500 |  | 600 | #2/0 | 11 |  | 600 | #1 | 9 | #2/0 | 11 | [11 empty] | #500 | 18 | 0.7073 |  | #500 | 18 | 0.7901 | 1.0082 | 0.7073 | 0.6984 | 0.6939 | 0.6151 | 0.5026 | #250 | 14 | 0.0847 | 0.0515 | 0.0847 | [11 empty] | 6 | #4 | #8 | [8 empty] | #500 | 18 | 0.7073 |  | #500 | 18 | 0.7901 | 1.0082 | 0.7073 | 0.6984 | 0.6939 | 0.6151 | 0.5026 | #250 | 14 | 0.0847 | 0.0515 | 0.0847
[14 empty] | LOAD | LOAD | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | HARMONIC |  | LOAD |  | LOAD |  | LOAD | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  | LOAD |  |  |  | 57 | 0 | 0 | ENTER CIRCUIT #57 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #57 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #57 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 600 |  | 800 | #3/0 | 12 |  | 800 | #1/0 | 10 | #3/0 | 12 | [24 empty] | #300 | 15 | 0.0707 | 0.0429 | 0.0707 |  |  | CALCULATED RESISTANCE OF CONDUCTOR(S) | [6 empty] | 0.808 |  | 7 | #3 | #8 | [8 empty] | PRIMARY | [12 empty] | #300 | 15 | 0.0707 | 0.0429 | 0.0707 |  |  | CALCULATED RESISTANCE OF CONDUCTOR(S) | [6 empty] | #N/A
[14 empty] | L1 | L2 | L3 |  | L1 |  | L2 |  | L3 |  | L1 |  | L2 |  | L3 |  | L1 |  | L2 |  | L3 |  | LOAD |  | L1 |  | L2 |  | L3 | L1 |  | L2 |  | L3 |  | L1 |  | L3 |  | L1 |  | L2 |  | L1 |  | L2 |  | L3 |  |  |  | 59 | 0 | 0 | ENTER CIRCUIT #59 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #59 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #59 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 800 |  | 1000 | #4/0 | 13 |  | 1000 | #2/0 | 11 | #4/0 | 13 | [11 empty] | L1-L3 WIRE CODE | 5 |  | L1,L3 | L2 | NET | # OF WIRES | [6 empty] | #350 | 16 | 0.0605 | 0.0367 | 0.0605 | [11 empty] | 8 | #2 | #8 | [8 empty] | LINE | #N/A |  | L1,L3 | L3 |  | # OF WIRES | [6 empty] | #350 | 16 | 0.0605 | 0.0367 | 0.0605
[14 empty] | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 61 | 0 | 0 | ENTER CIRCUIT #61 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #61 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #61 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 1000 |  | 1200 | #250 | 14 |  | 1200 | #3/0 | 12 | #250 | 14 | [11 empty] | L1-L3 SQ IN | 0.0507 | X | 2 | 0 | 1 | 3 | = | 0.1521 | 0.0507 | 0 | 1 | #6 | #400 | 17 | 0.0529 | 0.0321 | 0.0529 | [11 empty] | 9 | #1 | #6 | [8 empty] | LINE | #N/A | X | 2 | 0 |  | 2 | = | #N/A | #N/A | #N/A | 1 | #N/A | #400 | 17 | 0.0529 | 0.0321 | 0.0529
[38 empty] | 0 |  | 0 |  | 0 | [22 empty] | 63 | 0 | 0 | ENTER CIRCUIT #63 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #63 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #63 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT | [11 empty] | L2 WIRE CODE | 5 | [11 empty] | #500 | 18 | 0.0424 | 0.0258 | 0.0424 | [11 empty] | 10 | #1/0 | #6 | [21 empty] | #500 | 18 | 0.0424 | 0.0258 | 0.0424
[28 empty] | 0 |  | CONTINUOUS | [7 empty] | MAX | LINE LOAD | 0 | [6 empty] | TOTAL |  |  |  | 0 |  |  |  | 0 | [5 empty] | 0 |  |  |  | 65 | 0 | 0 | ENTER CIRCUIT #65 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #65 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #65 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: GROUND; WIRE AMPS: WIRE; WIRE AMPS: WIRE; WIRE AMPS: WIRE | [11 empty] | L2 SQ IN | 0.0507 | X |  | 0 |  | 0 | = | 0 | 0.0507 | 0 | 3 | #6 | WIRE CODE | 5 | 5 | 5 | 5 | [11 empty] | 11 | #2/0 | #4 | [21 empty] | WIRE CODE | #N/A
[16 empty] | 0 | [5 empty] | 0 | [7 empty] | LOAD | [8 empty] | X | 3 |  | TOTAL |  |  |  |  | KITCHEN | [17 empty] | 67 | 0 | 0 | ENTER CIRCUIT #67 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #67 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #67 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: MAX; WIRE AMPS: SIZE; WIRE AMPS: SIZE; WIRE AMPS: PER | [11 empty] | NET WIRE CODE | 5 | [11 empty] | WIRE RES | 0.808 | 0.808 | 0.808 | 0.808 | [11 empty] | 12 | #3/0 | #4 | [21 empty] | WIRE RES | #N/A
[30 empty] | 0 | [9 empty] | 0 |  | MOTOR |  |  |  |  | LOAD | [11 empty] | NEUTRAL LOAD >> |  | 0 |  |  |  | 69 | 0 | 0 | ENTER CIRCUIT #69 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #69 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #69 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: OVER CURRENT; WIRE AMPS: AWG; WIRE AMPS: CODE; WIRE AMPS: PHASE | [11 empty] | NET SQ IN | 0.0507 | X |  |  | 0 | 0 | = | 0 | 0.0507 | 0 | 4 | #6 | AMPS PER WIRE | 0 | 0 | 0 | 0 | [11 empty] | 13 | #4/0 | #2 | [21 empty] | AMPS PER WIRE | 0
[30 empty] | VA X .025 = | [11 empty] | LOAD |  |  |  |  | 0 | [17 empty] | 71 | 0 | 0 | ENTER CIRCUIT #71 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #71 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #71 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: 60; WIRE AMPS: #8; WIRE AMPS: 4; WIRE AMPS: 1 | [11 empty] | GND WIRE CODE | 4 | [27 empty] | 14 | #250 | #2 | [8 empty] | GROUND CODE | 4
[30 empty] | CONTINUOUS LOAD 0 VA X .025 = | [8 empty] | SECONDARY | 0 |  | 0 | [22 empty] | 73 | 0 | 0 | ENTER CIRCUIT #73 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #73 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #73 NEUTRAL IDENTIFIER ( N or SPACE ) | [28 empty] | GND SQ IN | 0.0366 | X |  |  |  | 1 | = | 0.0366 | 0.0366 | 5 | 0 | #8 | [16 empty] | 15 | #300 | #2 | [8 empty] | GND SQ IN | 0.0366 | X |  |  |  | 0 | = | 0 | 0.0366 |  | 0 | #8
[39 empty] | PRIMARY | 0 | [18 empty] | L1 | 0 |  |  |  |  | 75 | 0 | 0 | ENTER CIRCUIT #75 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #75 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #75 NEUTRAL IDENTIFIER ( N or SPACE ) | [57 empty] | 16 | #350 | #2
[59 empty] | L2 | 0 |  |  |  |  | 77 | 0 | 0 | ENTER CIRCUIT #77 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #77 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #77 NEUTRAL IDENTIFIER ( N or SPACE ) | [28 empty] | TOTAL AREA OF CONDUCTORS | [5 empty] | 4 |  | 0.1887 |  | 5 | 8 | [10 empty] | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 ) = 0.0 VD | [6 empty] | 17 | #400 | #1/0 | [8 empty] | TOTAL AREA OF CONDUCTORS | [5 empty] | 2 |  | #N/A |  | #N/A | 1 | [10 empty] | ( 2 X 0' L X 0.0000 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[59 empty] | L3 | 0 |  |  |  |  | 79 | 0 | 0 | ENTER CIRCUIT #79 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #79 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #79 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: GROUND SIZE MODULE PRIMARY | [18 empty] | (L2) | (N) | [20 empty] | 18 | #500 | #1/0
[65 empty] | 81 | 0 | 0 | ENTER CIRCUIT #81 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #81 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #81 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: GND Y/N? (NGYN); WIRE AMPS: 0 | [18 empty] | AL | [42 empty] | 0
[59 empty] | MAX | 0 |  |  |  |  | 83 | 0 | 0 | ENTER CIRCUIT #83 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #83 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #83 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: MAX AMPS (NMA); WIRE AMPS: 60 | [13 empty] | 3 | - | #6 |  | THHN | 3-#6 THHN AL | [8 empty] | 3D | 3D | [6 empty] | VD % | VD % | VD % | VD % |  |  | 50 | [15 empty] | 2 | - | #N/A |  | 0 | #N/A | [12 empty] | VD % | VD % | VD % | VD %
[65 empty] | 84 | 0 | 0 | CONNECTED ON (L2) LOAD MAY NOT EXCEED LOAD ON (L1 & L3) | [12 empty] | WIRE AMPS: CU/AL? (NCUAL2); WIRE AMPS: 0 | [13 empty] | 0 | - |  |  | THHN | [7 empty] | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3-PHASE Y | L2 | L1 & L3 |  |  |  | 75 C | 60º C | GROUND | 75 C | 90º C | WIRE | [9 empty] | 0 | - | #8 |  | GND | 0-#8 0 GND |  |  | 1-PHASE | 3Y |  |  |  | 1-PHASE | 3Y | L2 | L1 & L3 |  | 1-PHASE | 3-PHASE Y | L2 | L1 & L3
[64 empty] | 0 |  | 0 |  |  | 0 |  |  | 0 | [8 empty] | WIRE AMPS: GND_TABLE | [13 empty] | 0 | - |  |  | THHN | [6 empty] | 2 | 2 | 2 | 2 | 2 | ( | ( | ( | ( | ( | ( | ( | ( | ( | ( |  |  |  | AMPS | AMPS | WIRE | AMPS | AMPS | SIZE | [16 empty] | 2 | 2 | 2 |  |  | ( | ( | ( | ( | ( | ( | ( | ( | ( | (
[81 empty] | LOOKUP |  | RATING | SEL | SEL |  | RATING | CU | CU | AL | AL | [13 empty] | 1 | - | #8 |  | GND | 1-#8 AL GND | [5 empty] | X L | 50 | 50 | 50 | 50 | 2 | 2 | 2 | 2 | 2 | VD | 0.0 | 0.0 | 0.0 | 0.0 |  |  |  | CU | CU | SIZE | CU | CU | AWG | [16 empty] | X L | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | VD | #N/A | #N/A | 0.0 | 0.0
[65 empty] | 2 | 0 | 0 | ENTER CIRCUIT #2 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #2 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #2 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | GROUND |  | OVER | WIRE | WIRE |  | OVER | WIRE | WIRE | WIRE | WIRE | [24 empty] | X R | 0.808 | 0.808 | 0.808 | 0.808 | X | X | X | X | X | ÷ | VD ÷ | VD ÷ | VD ÷ | VD ÷ |  |  | 0 | 420 | 355 | #1/0 | 420 | 475 | #600 | [16 empty] | X R | #N/A | #N/A |  |  | X | X | X | X | X | ÷ | VD ÷ | VD ÷ | VD ÷ | VD ÷
[65 empty] | 4 | 0 | 0 | ENTER CIRCUIT #4 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #4 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #4 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | AMPS |  | CURRENT | SIZE | CODE |  | CURRENT | SIZE | CODE | SIZE | CODE | [24 empty] | X I | 0 | 0 | 0 | 0 | L | 50 | 50 | 50 | 50 | VOLTS | 240 | 240 | 240 | 240 |  |  | 420.001 | 460 | 385 | #2/0 | 460 | 520 | #700 | [16 empty] | X I | 0 | 0 |  |  | L | 0 | 0 | 0 | 0 | VOLTS | 240 | 240 | 240 | 240
[65 empty] | 6 | 0 | 0 | ENTER CIRCUIT #6 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #6 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #6 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 0 |  | 60 | #8 | 4 |  | 60 | #10 | 3 | #8 | 4 | [18 empty] | 3-#6 THHN AL | [5 empty] | = |  |  |  |  | X | ' L X | ' L X | ' L X | ' L X | X | V X | V X | V X | V X |  |  | 460.001 | 475 | 400 | #2/0 | 475 | 535 | #750 | [16 empty] | = |  |  |  |  | X | ' L X | ' L X | ' L X | ' L X | X | V X | V X | V X | V X
[65 empty] | 8 | 0 | 0 | ENTER CIRCUIT #8 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #8 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #8 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 60 |  | 100 | #6 | 5 |  | 100 | #8 | 4 | #6 | 5 | [18 empty] | 1-#8 AL GND | [5 empty] | ÷ 1000 | 1000 | 1000 | 1000 | 1000 | R | 0.8080 | 0.8080 | 0.8080 | 0.8080 | 100 | 100 | 100 | 100 | 100 |  |  | 475.001 | 490 | 410 | #2/0 | 490 | 555 | #800 | [16 empty] | ÷ 1000 | 1000 | 1000 |  |  | R | #N/A | #N/A | 0.0000 | 0.0000 | 100 | 100 | 100 | 100 | 100
[65 empty] | 10 | 0 | 0 | ENTER CIRCUIT #10 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #10 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #10 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 100 |  | 200 | #4 | 6 |  | 200 | #6 | 5 | #4 | 6 | [24 empty] | = |  |  |  |  | X | R X | R X | R X | R X | ) = | ) = | ) = | ) = | ) = |  |  | 490.001 | 520 | 435 | #2/0 | 520 | 585 | #900 | [16 empty] | = |  |  |  |  | X | R X | R X | R X | R X | ) = | ) = | ) = | ) = | ) =
[65 empty] | 12 | 0 | 0 | ENTER CIRCUIT #12 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #12 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #12 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 200 |  | 300 | #2 | 8 |  | 300 | #4 | 6 | #2 | 8 | [24 empty] | X 0.866 | 1 | 0.866 | 0.866 | 1 | I | 0.0 | 0.0 | 0.0 | 0.0 | VD | 0.0 | 0.0 | 0.0 | 0.0 |  |  | 520.001 | 545 | 455 | #2/0 | 545 | 615 | #1000 | [16 empty] | X 0.866 | 1 | 0.866 |  |  | I | 0.0 | 0.0 | 0.0 | 0.0 | VD | #N/A | #N/A | 0.0 | 0.0
[65 empty] | 14 | 0 | 0 | ENTER CIRCUIT #14 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #14 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #14 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 300 |  | 400 | #1 | 9 |  | 400 | #3 | 7 | #1 | 9 | [24 empty] | = VD | 0 | 0 | 0 | 0 | / | A ÷ | A ÷ | A ÷ | A ÷ | % | % VD | % VD | % VD | % VD |  |  | 545.001 | 590 | 495 | #3/0 | 590 | 665 | #1250 | [16 empty] | = VD | #N/A | #N/A |  |  | / | A ÷ | A ÷ | A ÷ | A ÷ | % | % VD | % VD | % VD | % VD
[65 empty] | 16 | 0 | 0 | ENTER CIRCUIT #16 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #16 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #16 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 400 |  | 500 | #1/0 | 10 |  | 500 | #2 | 8 | #1/0 | 10 | [24 empty] | ÷ VOLTS | 240 | 240 | 240 | 240 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | ( VD ÷ VOLTS X 100 ) = VD % | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD |  |  | 590.001 | 625 | 520 | #3/0 | 625 | 705 | #1500 | [16 empty] | ÷ VOLTS | 240 | 240 |  |  | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | ( VD ÷ VOLTS X 100 ) = VD % | #N/A | #N/A | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[65 empty] | 18 | 0 | 0 | ENTER CIRCUIT #18 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #18 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #18 NEUTRAL IDENTIFIER ( N or SPACE ) |  |  |  |  | GROUND |  | 500 |  | 600 | #2/0 | 11 |  | 600 | #1 | 9 | #2/0 | 11 | [24 empty] | = VD % | 0% | 0% | 0% | 0% | ) | ) | X | X | ) |  | 0.0 % VD | 0.0 % VD | 0.0 % VD | 0.0 % VD |  |  | 625.001 | 650 | 545 | #3/0 | 650 | 735 | #1750 | [16 empty] | = VD % | #N/A | #N/A |  |  | X | ) | X | X | ) |  | #N/A | #N/A | 0.0 % VD | 0.0 % VD
[65 empty] | 20 | 0 | 0 | ENTER CIRCUIT #20 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #20 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #20 NEUTRAL IDENTIFIER ( N or SPACE ) |  |  |  |  | OVERGROUNDWIRE |  | 600 |  | 800 | #3/0 | 12 |  | 800 | #1/0 | 10 | #3/0 | 12 | [29 empty] | 0.866 | = | 0.866 | 0.866 | = | [7 empty] | 650.001 | 665 | 560 | #3/0 | 665 | 750 | #2000 | [21 empty] | 0.866 | = | 0.866 | 0.866 | =
[65 empty] | 22 | 0 | 0 | ENTER CIRCUIT #22 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #22 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #22 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | 800 |  | 1000 | #4/0 | 13 |  | 1000 | #2/0 | 11 | #4/0 | 13 | [29 empty] | ) | 0.0 | ) | ) | 0.0 |  | 0.0 % VD | 0.0 % VD | 0.0 % VD | 0.0 % VD | [30 empty] | ) | #N/A | ) | ) | 0.0
[65 empty] | 24 | 0 | 0 | ENTER CIRCUIT #24 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #24 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #24 NEUTRAL IDENTIFIER ( N or SPACE ) |  |  |  | FEEDER CONDUIT |  |  | 1000 |  | 1200 | #250 | 14 |  | 1200 | #3/0 | 12 | #250 | 14 | [29 empty] | = | VD | = | = | VD | [7 empty] | #1/0 | [27 empty] | = | VD | = | = | VD
[65 empty] | 26 | 0 | 0 | ENTER CIRCUIT #26 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #26 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #26 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT; WIRE AMPS: OUTPUT | [29 empty] | VD |  | 0.0 | 0.0 |  |  |  | 0.0 % VD | [32 empty] | VD |  | #N/A | 0.0
[65 empty] | 28 | 0 | 0 | ENTER CIRCUIT #28 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #28 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #28 NEUTRAL IDENTIFIER ( N or SPACE ) |  |  |  | 0 |  |  | WIRE AMPS: GROUND; WIRE AMPS: WIRE; WIRE AMPS: WIRE; WIRE AMPS: WIRE | [31 empty] | VD | VD | [38 empty] | VD | VD
[65 empty] | 30 | 0 | 0 | ENTER CIRCUIT #30 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #30 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #30 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: MAX; WIRE AMPS: SIZE; WIRE AMPS: SIZE; WIRE AMPS: PER | [36 empty] | 0.0 % VD
[65 empty] | 32 | 0 | 0 | ENTER CIRCUIT #32 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #32 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #32 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: OVER CURRENT; WIRE AMPS: AWG; WIRE AMPS: CODE; WIRE AMPS: PHASE | [30 empty] | 0.0 VD | 0.0 VD | 0.0 VD | 0.0 VD | [36 empty] | #N/A | #N/A | 0.0 VD | 0.0 VD
[65 empty] | 34 | 0 | 0 | ENTER CIRCUIT #34 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #34 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #34 NEUTRAL IDENTIFIER ( N or SPACE ) | [6 empty] | WIRE AMPS: 60; WIRE AMPS: #8; WIRE AMPS: 4; WIRE AMPS: #N/A | [30 empty] | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 ) = 0.0 VD | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 ) = 0.0 VD | [36 empty] | #N/A | #N/A | ( 2 X 0' L X 0.0000 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD | ( 2 X 0' L X 0.0000 R X 0.0 A ÷ 1,000 ) = 0.0 VD
[65 empty] | 36 | 0 | 0 | ENTER CIRCUIT #36 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #36 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #36 NEUTRAL IDENTIFIER ( N or SPACE )
[65 empty] | 38 | 0 | 0 | ENTER CIRCUIT #38 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #38 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #38 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | WIRE | WIRE | [13 empty] | 1 | [24 empty] | WIRE | WIRE
[65 empty] | 40 | 0 | 0 | ENTER CIRCUIT #40 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #40 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #40 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | SIZE | WIRE | [38 empty] | SIZE | WIRE | [12 empty] | PRIMARY VD | #N/A
[65 empty] | 42 | 0 | 0 | ENTER CIRCUIT #42 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #42 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #42 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | CODE | SIZE | [11 empty] | L1 L3 | VD % | 0.0 | [24 empty] | CODE | SIZE
[65 empty] | 44 | 0 | 0 | ENTER CIRCUIT #44 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #44 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #44 NEUTRAL IDENTIFIER ( N or SPACE ) | [39 empty] | AWG | [39 empty] | AWG
[65 empty] | 46 | 0 | 0 | ENTER CIRCUIT #46 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #46 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #46 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 3 | #10 | [11 empty] | L2 | VD % | 0.0 | [24 empty] | 3 | #10
[65 empty] | 48 | 0 | 0 | ENTER CIRCUIT #48 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #48 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #48 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 4 | #8 | [38 empty] | 4 | #8
[65 empty] | 50 | 0 | 0 | ENTER CIRCUIT #50 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #50 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #50 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 5 | #6 | [5 empty] | VOLTAGE DROP | [32 empty] | 5 | #6 | [5 empty] | VOLTAGE DROP
[65 empty] | 52 | 0 | 0 | ENTER CIRCUIT #52 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #52 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #52 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 6 | #4 | [5 empty] | Single Phase | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 ) = 0.0 VD |  |  | Voltage Drop % | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | [27 empty] | 6 | #4 | [5 empty] | Single Phase Primary | #N/A |  |  | Voltage Drop % Primary | #N/A
[65 empty] | 54 | 0 | 0 | ENTER CIRCUIT #54 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #54 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #54 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 7 | #3 | [5 empty] | Three Phase | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD |  |  | Voltage Drop % | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | [27 empty] | 7 | #3 | [5 empty] | Three Phase Primary | #N/A |  |  | Voltage Drop % Primary | #N/A
[65 empty] | 56 | 0 | 0 | ENTER CIRCUIT #56 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #56 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #56 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 8 | #2 | [5 empty] | Voltage Drop L1 & L3 | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 ) = 0.0 VD |  |  | Voltage Drop % L1 & L3 | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | [27 empty] | 8 | #2 | [5 empty] | Voltage Drop L1 & L3 | ( 2 X 0' L X 0.0000 R X 0.0 A ÷ 1,000 ) = 0.0 VD |  |  | Voltage Drop % L1 & L3 | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[65 empty] | 58 | 0 | 0 | ENTER CIRCUIT #58 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #58 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #58 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 9 | #1 | [5 empty] | Voltage Drop L2 ( Hi-Leg ) | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD |  |  | Voltage Drop % L2 ( Hi-Leg ) | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD | [27 empty] | 9 | #1 | [5 empty] | Voltage Drop L2 ( Hi-Leg ) | ( 2 X 0' L X 0.0000 R X 0.0 A ÷ 1,000 X 0.866 ) = 0.0 VD |  |  | Voltage Drop % L2 ( Hi-Leg ) | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
[65 empty] | 60 | 0 | 0 | ENTER CIRCUIT #60 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #60 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #60 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 10 | #1/0 | [38 empty] | 10 | #1/0
[65 empty] | 62 | 0 | 0 | ENTER CIRCUIT #62 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #62 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #62 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 11 | #2/0 | [38 empty] | 11 | #2/0
[65 empty] | 64 | 0 | 0 | ENTER CIRCUIT #64 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #64 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #64 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 12 | #3/0 | [38 empty] | 12 | #3/0
[65 empty] | 66 | 0 | 0 | ENTER CIRCUIT #66 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #66 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #66 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 13 | #4/0 | [38 empty] | 13 | #4/0
[65 empty] | 68 | 0 | 0 | ENTER CIRCUIT #68 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #68 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #68 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 14 | #250 | [38 empty] | 14 | #250
[65 empty] | 70 | 0 | 0 | ENTER CIRCUIT #70 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #70 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #70 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 15 | #300 | [38 empty] | 15 | #300
[65 empty] | 72 | 0 | 0 | ENTER CIRCUIT #72 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #72 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #72 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 16 | #350 | [38 empty] | 16 | #350
[65 empty] | 74 | 0 | 0 | ENTER CIRCUIT #74 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #74 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #74 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 17 | #400 | [38 empty] | 17 | #400
[65 empty] | 76 | 0 | 0 | ENTER CIRCUIT #76 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #76 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #76 NEUTRAL IDENTIFIER ( N or SPACE ) | [38 empty] | 18 | #500 | [38 empty] | 18 | #500
[65 empty] | 78 | 0 | 0 | ENTER CIRCUIT #78 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #78 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #78 NEUTRAL IDENTIFIER ( N or SPACE )
[65 empty] | 80 | 0 | 0 | ENTER CIRCUIT #80 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #80 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #80 NEUTRAL IDENTIFIER ( N or SPACE )
[65 empty] | 82 | 0 | 0 | ENTER CIRCUIT #82 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #82 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #82 NEUTRAL IDENTIFIER ( N or SPACE )
[65 empty] | 84 | 0 | 0 | ENTER CIRCUIT #84 LOAD IDENTIFIER ( G, D, C, M, K ) | 0 | 0 | ENTER CIRCUIT #84 HARMONIC IDENTIFIER ( H, or SPACE ) | 0 | 0 | ENTER CIRCUIT #84 NEUTRAL IDENTIFIER ( N or SPACE )
[64 empty] | 0 |  | 0 |  |  | 0 |  |  | 0
PRIMARY
[66 empty] | AC/AL | AC/AL
[66 empty] | ERROR | ERROR
[66 empty] | CHECK | CHECK
[65 empty] | CU/AL? | AL | 0
[65 empty] | AM72-CA | 0 | 0
[65 empty] | THHN-CA | 0 | 0
[65 empty] | XHHW-CA | 0 | 0
[66 empty] | 0 | 0

## S-Sec Cable (hidden)
[7 empty] | SHORT | WIRE | WIRE | GROUND | MAX |  |  |  | 3-COND W/GND SER CABLE AL
[7 empty] | C VALUE | RES | SIZE | SIZE | AMPS | [14 empty] | AMPACITY TABLE
AMPS | 0 | 1 | SER 3C AL | SER CABLE | 3-#6 AL | 1-#6 GND | 1482 | 0.808 | #6 | #6 | 50 | 6-6-6-6 | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
WIRE TEMP | 75 | 0 | SER 3C CU | SER CABLE | 3-#6 CU | 1-#6 GND | 2433 | 0.491 | #6 | #6 | 65 | 6-6-6-6 | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
# OF CONDUCTORS | 3 | 0 | SER 4C AL | SER CABLE | 4-#6 AL | 1-#6 GND | 1482 | 0.808 | #6 | #6 | 50 | 6-6-6-6-6 | [5 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
CU OR AL | AL | 0 | ROMEX 3C CU | ROMEX | 3-#6 CU | 1-#10 GND | 2433 | 0.491 | #6 | #10 | 65 | 6-6-6-6 |  |  |  | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
FEEDER TYPE | SER | 0 | MC 3C AL | MC CABLE | 3-#6 AL | 1-#6 GND | 1482 | 0.808 | #6 | #6 | 50 | 6-6-6-6 |  |  |  | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
|  | 0 | MC 4C AL | MC CABLE | 4-#6 AL | 1-#6 GND | 1482 | 0.808 | #6 | #6 | 50 | 6-6-6-6-6 |  |  |  | 102 | 65 | 2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3740 | 0.319 | #2 | 75 | 90 | 100
|  | 0 | MC 3C CU | MC CABLE | 3-#4 CU | 1-#8 GND | 3830 | 0.308 | #4 | #8 | 85 | 4-4-4-8 |  |  |  | 103 | 90 | 1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 | #1 | 85 | 100 | 115
|  | 0 | MC 4C CU | MC CABLE | 4-#4 CU | 1-#8 GND | 3830 | 0.308 | #4 | #8 | 85 | 4-4-4-4-8 |  |  |  | 104 | 100 | 1/0-1/0-1/0-2 | #1/0 | #2 | 120 | 10 | 104 | 5876 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-1 | #2/0 | #1 | 135 | 11 | 105 | 7373 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 155 | 12 | 106 | 9243 | 0.126 | #3/0 | 130 | 155 | 175
|  |  | SER 3C AL | SER CABLE | 3-#6 AL | 1-#6 GND | 1482 | 0.808 | #6 | #6 | 50 | 6-6-6-6 |  |  |  | 107 | 155 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 180 | 13 | 107 | 11409 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | EXCEED | EXCEED | EXCEED | 180 | EXCEED | 108 | EXCEED | EXCEED
|  |  | SER 3C AL | SER CABLE | 3-#6 AL | 1-#6 GND | 1482 | 0.808 | #6 | #6 | 50 | 6-6-6-6
[16 empty] | 100 |  | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 3- | #6 | AL |  |  | 3-#6 AL
|  |  | THE DESIGN LOAD OF | 0 | AMPS EXCEEDS THE MAXIMUM |  |  |  | THE DESIGN LOAD OF 0 AMPS EXCEEDS THE MAXIMUM | [8 empty] | 1- | #6 | GND |  |  | 1-#6 GND
|  |  | CABLE RATING OF | 50 | AMPS |  |  |  | CABLE RATING OF 50 AMPS
3-COND W/GND SER CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TEMP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | CU | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 65 | 5 | 100 | 2433 | 0.491 | #6 | 55 | 65 | 75
[16 empty] | 101 | 65 | 4-4-4-6 | #4 | #6 | 85 | 6 | 101 | 3838 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 102 | 85 | 3-3-3-5 | #3 | #5 | 100 | 7 | 102 | 4833 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 103 | 100 | 2-2-2-4 | #2 | #4 | 115 | 8 | 103 | 6087 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 104 | 115 | 1-1-1-3 | #1 | #3 | 130 | 9 | 104 | 7579 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 105 | 130 | 1/0-1/0-1/0-2 | #1/0 | #2 | 150 | 10 | 105 | 9473 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 106 | 150 | 2/0-2/0-2/0-1 | #2/0 | #1 | 175 | 11 | 106 | 11703 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 107 | 175 | 3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 200 | 12 | 107 | 14410 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 108 | 200 | 4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 230 | 13 | 108 | 17483 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 109 | 230 | EXCEED | EXCEED | EXCEED | 230 | EXCEED | 109 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6 | #6 | #6 | 65 | 5 | 100 | 2433 | 0.491
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 3- | #6 | CU |  |  | 3-#6 CU
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
4-COND W/GND SER CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3740 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 90 | 1-1-1-1-3 | #1 | #3 | 100 | 9 | 103 | 4699 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 100 | 1/0-1/0-1/0-1/0-2 | #1/0 | #2 | 120 | 10 | 104 | 5876 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-2/0-1 | #2/0 | #1 | 135 | 11 | 105 | 7373 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-3/0-1/0 | #3/0 | #1/0 | 155 | 12 | 106 | 9243 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 155 | 4/0-4/0-4/0-4/0-2/0 | #4/0 | #2/0 | 180 | 13 | 107 | 11409 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | 250-250-250-250-3/0 | #250 | #3/0 | 205 | 14 | 108 | 13236 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 205 | 300-300-300-300-4/0 | #300 | #4/0 | 230 | 15 | 109 | 15495 | 0.0707 | #300 | 190 | 230 | 255
[16 empty] | 110 | 230 | EXCEED | EXCEED | EXCEED | 230 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808
[18 empty] | SER CABLE |  |  |  |  | SER CABLE
[18 empty] | 4- | #6 | AL |  |  | 4-#6 AL
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
3-COND W/GND ROMEX CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #10 | 65 | 5 | 100 | 2433 | 0.491 | #6 | 55 | 65 | 75
[16 empty] | 101 | 65 | 4-4-4-4 | #4 | #8 | 85 | 6 | 101 | 3838 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 102 | 85 | 2-2-2-2 | #2 | #8 | 115 | 7 | 102 | 4833 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 115 | EXCEED | EXCEED | EXCEED | 115 | EXCEED | 103 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6 | #6 | #10 | 65 | 5 | 100 | 2433 | 0.491
[18 empty] | ROMEX |  |  |  |  | ROMEX
[18 empty] | 3- | #6 | CU |  |  | 3-#6 CU
[18 empty] | 1- | #10 | GND |  |  | 1-#10 GND
3-COND W/GND MC CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 50 | 4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 65 | 2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3734 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 90 | 1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 100 | 1/0-1/0-1/0-4 | #1/0 | #4 | 120 | 10 | 104 | 5852 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-4 | #2/0 | #4 | 135 | 11 | 105 | 7327 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-4 | #3/0 | #4 | 155 | 12 | 106 | 9077 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 155 | 4/0-4/0-4/0-2 | #4/0 | #2 | 180 | 13 | 107 | 11185 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | 250-250-250-2 | #250 | #2 | 205 | 14 | 108 | 12797 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 205 | 350-350-350-1 | #300 | #1 | 250 | 16 | 109 | 16795 | 0.0605 | #350 | 210 | 250 | 280
[16 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 3- | #6 | AL |  |  | 3-#6 AL
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
4-COND W/GND MC CABLE AL
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | AL | AWG | AL | AL | AL
[16 empty] | 100 | 0 | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808 | #6 | 40 | 50 | 60
[16 empty] | 101 | 50 | 4-4-4-4-6 | #4 | #6 | 65 | 6 | 101 | 2353 | 0.508 | #4 | 55 | 65 | 75
[16 empty] | 102 | 65 | 2-2-2-2-4 | #2 | #4 | 90 | 8 | 102 | 3734 | 0.319 | #2 | 75 | 90 | 100
[16 empty] | 103 | 90 | 1-1-1-1-4 | #1 | #4 | 100 | 9 | 103 | 4686 | 0.253 | #1 | 85 | 100 | 115
[16 empty] | 104 | 100 | 1/0-1/0-1/0-1/0-4 | #1/0 | #4 | 120 | 10 | 104 | 5852 | 0.201 | #1/0 | 100 | 120 | 135
[16 empty] | 105 | 120 | 2/0-2/0-2/0-2/0-4 | #2/0 | #4 | 135 | 11 | 105 | 7327 | 0.159 | #2/0 | 115 | 135 | 150
[16 empty] | 106 | 135 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 155 | 12 | 106 | 9077 | 0.126 | #3/0 | 130 | 155 | 175
[16 empty] | 107 | 155 | 4/0-4/0-4/0-4/0-2 | #4/0 | #2 | 180 | 13 | 107 | 11185 | 0.1 | #4/0 | 150 | 180 | 205
[16 empty] | 108 | 180 | 250-250-250-250-1 | #250 | #1 | 205 | 14 | 108 | 12797 | 0.0847 | #250 | 170 | 205 | 230
[16 empty] | 109 | 205 | 350-350-350-350-1/0 | #350 | #1/0 | 250 | 16 | 109 | 16795 | 0.0605 | #350 | 210 | 250 | 280
[16 empty] | 110 | 250 | EXCEED | EXCEED | EXCEED | 250 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 6-6-6-6-6 | #6 | #6 | 50 | 5 | 100 | 1482 | 0.808
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 4- | #6 | AL |  |  | 4-#6 AL
[18 empty] | 1- | #6 | GND |  |  | 1-#6 GND
3-COND W/GND MC CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | GROUND | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 101 | 85 | 3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 102 | 100 | 2-2-2-6 | #2 | #6 | 115 | 8 | 102 | 5989 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 115 | 1-1-1-6 | #1 | #6 | 130 | 9 | 103 | 7454 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 104 | 130 | 1/0-1/0-1/0-6 | #1/0 | #6 | 150 | 10 | 104 | 9210 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 105 | 150 | 2/0-2/0-2/0-6 | #2/0 | #6 | 175 | 11 | 105 | 11245 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 106 | 175 | 3/0-3/0-3/0-4 | #3/0 | #4 | 200 | 12 | 106 | 13656 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 107 | 200 | 4/0-4/0-4/0-4 | #4/0 | #4 | 230 | 13 | 107 | 16392 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 108 | 230 | 250-250-250-4 | #250 | #4 | 255 | 14 | 108 | 18311 | 0.0515 | #250 | 215 | 255 | 290
[16 empty] | 109 | 255 | 350-350-350-3 | #350 | #3 | 310 | 16 | 109 | 22646 | 0.0367 | #350 | 260 | 310 | 350
[16 empty] | 110 | 310 | EXCEED | EXCEED | EXCEED | 310 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 3- | #4 | CU |  |  | 3-#4 CU
[18 empty] | 1- | #8 | GND |  |  | 1-#8 GND
4-COND W/GND MC CABLE CU
AMPACITY TABLE
[13 empty] | AMPS | 0 |  | ROW | LOOKUP | WIRE | WIRE | NEUTRAL | 75 C | WIRE | ROW | SHORT | RES | WIRE | 60º C | 75 C | 90º C
[13 empty] | WIRE TMEP | 75 |  | SELECT |  | SIZE | SIZE | SIZE | AMPS | SIZE | SELECT | C VALUE | NEC | SIZE | AMPS | AMPS | AMPS
[18 empty] | AWG |  |  | AL | NUMBER |  |  | CU | AWG | CU | CU | CU
[16 empty] | 100 | 0 | 4-4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308 | #4 | 70 | 85 | 95
[16 empty] | 101 | 85 | 3-3-3-3-6 | #3 | #6 | 100 | 7 | 101 | 4820 | 0.245 | #3 | 85 | 100 | 110
[16 empty] | 102 | 100 | 2-2-2-2-6 | #2 | #6 | 115 | 8 | 102 | 5989 | 0.194 | #2 | 95 | 115 | 130
[16 empty] | 103 | 115 | 1-1-1-1-6 | #1 | #6 | 130 | 9 | 103 | 7454 | 0.154 | #1 | 110 | 130 | 150
[16 empty] | 104 | 130 | 1/0-1/0-1/0-1/0-6 | #1/0 | #6 | 150 | 10 | 104 | 9210 | 0.122 | #1/0 | 125 | 150 | 170
[16 empty] | 105 | 150 | 2/0-2/0-2/0-2/0-6 | #2/0 | #6 | 175 | 11 | 105 | 11245 | 0.0967 | #2/0 | 145 | 175 | 195
[16 empty] | 106 | 175 | 3/0-3/0-3/0-3/0-4 | #3/0 | #4 | 200 | 12 | 106 | 13656 | 0.0766 | #3/0 | 165 | 200 | 225
[16 empty] | 107 | 200 | 4/0-4/0-4/0-4/0-4 | #4/0 | #4 | 230 | 13 | 107 | 16392 | 0.0608 | #4/0 | 195 | 230 | 260
[16 empty] | 108 | 230 | 250-250-250-250-4 | #250 | #4 | 255 | 14 | 108 | 18311 | 0.0515 | #250 | 215 | 255 | 290
[16 empty] | 109 | 255 | 350-350-350-350-3 | #350 | #3 | 310 | 16 | 109 | 22646 | 0.0367 | #350 | 260 | 310 | 350
[16 empty] | 110 | 310 | EXCEED | EXCEED | EXCEED | 310 | EXCEED | 110 | EXCEED | EXCEED
[16 empty] | 100 |  | 4-4-4-4-8 | #4 | #8 | 85 | 6 | 100 | 3830 | 0.308
[18 empty] | MC CABLE |  |  |  |  | MC CABLE
[18 empty] | 4- | #4 | CU |  |  | 4-#4 CU
[18 empty] | 1- | #8 | GND |  |  | 1-#8 GND

## S-Schedule (hidden)
THIS SUB PANEL IS NOT BEING USED
SUB PANEL |  | HP2 |  |  |  |  | FEEDER |  |  |  |  | MASTER
FED FROM |  | CP1 |  |  |  |  | NUMBER OF CABLES |  | 1 |  |  | ERROR
# CIRCUITS |  |  |  | 84 |  |  | FEEDER CABLE |  | SER CABLE |  |  | 999
HI VOLTAGE |  |  |  | 240 |  |  | WIRE SIZE L1 |  | #6
LOW VOLTAGE |  |  |  | 120 |  |  | WIRE SIZE L2 |  | #6
PHASE |  |  |  | 1 | [7 empty] | MAIN BKR | Y
DESIGN LOAD AMPS |  |  |  | 0 |  |  | WIRE SIZE NEUTRAL |  | #6 |  |  | HI LEG | 0
NEUTRAL BUS |  |  |  | YES |  |  | WIRE SIZE GROUND |  | #6
GROUND BUS |  |  |  | YES
AVAILABLE FAULT CURRENT AT THIS PANEL |  |  |  | 2,892
MAIN BREAKER SIZE AMPS |  |  |  | 60 | [7 empty] | TRANSFORMER
0
# | BKR | CIRCUIT DESCRIPTION | I | VA |  | VA | I | CIRCUIT DESCRIPTION | BKR | #
1 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 2 | 0
3 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 4 | 0
5 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 6 | 0
7 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 8 | 0
9 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 10 | 0
11 |  | PINK CELLS ARE | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 12 | 0
13 |  | PROTECTED IN DEMO | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 14 | 0
15 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 16 | 0
17 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 18 | 0
19 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 20 | 0
21 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 22 | 0
23 |  |  | G |  | L2 | 1100 | G | LIGHTS | 20A-1P | 24 | 0
25 |  |  | G |  | L1 | 1100 | G | LIGHTS | 20A-1P | 26 | 0
27 |  |  | G |  | L2 |  | G |  |  | 28 | 0
29 |  |  | G |  | L1 |  | G |  |  | 30 | 0
31 |  |  | G |  | L2 |  | G |  |  | 32 | 0
33 |  |  | G |  | L1 |  | G |  |  | 34 | 0
35 |  |  | G |  | L2 |  | G |  |  | 36 | 0
37 |  |  | G |  | L1 |  | G |  |  | 38 | 0
39 |  |  | G |  | L2 |  | G |  |  | 40 | 0
41 |  |  | G |  | L1 |  | G |  |  | 42 | 0
43 |  |  | G |  | L2 |  | G |  |  | 44 | 0
45 |  |  | G |  | L1 |  | G |  |  | 46 | 0
47 |  |  | G |  | L2 |  | G |  |  | 48 | 0
49 |  |  | G |  | L1 |  | G |  |  | 50 | 0
51 |  |  | G |  | L2 |  | G |  |  | 52 | 0
53 |  |  | G |  | L1 |  | G |  |  | 54 | 0
55 |  |  | G |  | L2 |  | G |  |  | 56 | 0
57 |  |  | G |  | L1 |  | G |  |  | 58 | 0
59 |  |  | G |  | L2 |  | G |  |  | 60 | 0
61 |  |  | G |  | L1 |  | G |  |  | 62 | 0
63 |  |  | G |  | L2 |  | G |  |  | 64 | 0
65 |  |  | G |  | L1 |  | G |  |  | 66 | 0
67 |  |  | G |  | L2 |  | G |  |  | 68 | 0
69 |  |  | G |  | L1 |  | G |  |  | 70 | 0
71 |  |  | G |  | L2 |  | G |  |  | 72 | 0
73 |  |  | G |  | L1 |  | G |  |  | 74 | 0
75 |  |  | G |  | L2 |  | G |  |  | 76 | 0
77 |  |  | G |  | L1 |  | G |  |  | 78 | 0
79 |  |  | G |  | L2 |  | G |  |  | 80 | 0
81 |  |  | G |  | L1 |  | G |  |  | 82 | 0
83 |  |  | G |  | L2 |  | G |  |  | 84 | 0

## S-Calcs (hidden)
[11 empty] | 0 | [22 empty] | MAX
LOAD CALCULATIONS FOR "PANEL HP2" | [8 empty] | BASED ON THE 2008 NEC |  |  | FEED PANEL PHASE | 3Y |  |  |  | RECEPTACLE | L1 | L2 | L3 | TOTAL |  | RECEPTACLE | L1 | L2 | L3 | TOTAL |  | RECEPTACLE | L1 | L2 | L3 | TOTAL | MOTOR | L1 | L2 | L3
BASED ON THE 2008 NEC | [11 empty] | SOURCE PHASE | NONE |  |  |  | DIVERSITY | 0 | 0 |  | 0 |  | DIVERSITY | 0 |  | 0 | 0 |  | DIVERSITY | 0 | 0 | 0 | 0 | EXPORT | 0 | 0 | 0
|  |  | L1 |  | L2 | [12 empty] | 10000 | 10000 |  |  |  |  | 10000 |  | 10000 |  |  |  | 10000 | 10000 | 10000
CALCULATED LOAD ( NEC 215.5 ) |  |  | 0 | VA | 0 | VA |  |  |  |  | 999 |  | 1 |  |  |  | 1-PHASE | #DIV/0! | #DIV/0! |  | #DIV/0! |  | 3-PHASE DELTA | #DIV/0! |  | #DIV/0! | #DIV/0! |  | 3-PHASE Y | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| THIS SUB PANEL IS NOT BEING USED | [10 empty] | PHASE | 1 |  |  |  |  | #DIV/0! | #DIV/0! |  | #DIV/0! |  |  | #DIV/0! |  | #DIV/0! | #DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
CALCULATED LOAD WITH DEMAND FACTORS ( NEC 215.5 ) | [11 empty] | HI VOTLS | 240 |  |  |  | FIRST 10,000 W | 0 | 0 |  |  |  | FIRST 10,000 W | 0 |  | 0 | 0 |  | FIRST 10,000 W | 0 | 0 | 0 | 0
| GENERAL LOAD |  | 0 | VA | 0 | VA | [5 empty] | LOW VOTLS | 120 | [7 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
| RECEPTACLE LOAD (NEC 220.14) | [10 empty] | KITCHEN LOADS | 0
|  | 1ST 10,000W | 0 | VA | 0 | VA | [5 empty] | NEUTRAL SIZE | 0 | [9 empty] | L1 | L2 | L3
[12 empty] | HI-LEG SIZE | 0 |  |  |  | KITCHEN | 1 | 1 |  |  |  | 0 | 0 |  |  |  |  | OUTPUT
| CONTINUOUS LOAD (NEC 215.2) |  | 0 | VA | 0 | VA | [5 empty] | FACTOR | 0 |  |  |  | LOADS | 2 | 1 | [9 empty] | GENERAL LOAD | 0 | 0 | 0
|  | PLUS 25% | 0 | VA | 0 | VA | [5 empty] | FACTOR L2 | 0 |  |  |  |  | 3 | 0.9 | [9 empty] | RECEPTACLE LOAD | 0 | 0 | 0
| MOTOR LOAD (NEC 430.24) |  | 0 | VA | 0 | VA | [5 empty] | TRANS 0 OR 1 | 0 |  |  |  |  | 4 | 0.8 | [9 empty] | CONTINUOUS LOAD | 0 | 0 | 0
|  | PLUS 25% OF LARGEST MOTOR | 0 | VA | 0 | VA | [5 empty] | PHASE SOURCE | NONE |  |  |  |  | 5 | 0.7 | [9 empty] | MOTOR LOAD | 0 | 0 | 0
| KITCHEN LOAD (NEC 220.56) | [10 empty] | FAULT METHOD | YES |  |  |  |  | 6 | 0.65 | [9 empty] | KITCHEN LOADS | 0 | 0 | 0
|  | L1 ( 0 X 1 ) = | 0 | VA | [7 empty] | VD CALCS | YES |  |  |  | 1
|  | L2 ( 0 X 1 ) = |  |  | 0 | VA | [5 empty] | SUBFEED | NONE | [15 empty] | TOTALS | 0 | 0 | 0
[17 empty] | L1 ( | 0 | 0 | X | 1 | ) = | L1 ( 0 X 1 ) =
|  |  | 0 | VA | 0 | VA | 0 |  |  | 0 |  | L1 | 0 |  |  |  | L2 ( | 0 | 0 | X | 1 | ) = | L2 ( 0 X 1 ) =
TOTAL BALANCED LOAD (1-PHASE) |  |  | 0 | VA | 0 | VA | 0 | VA |  |  |  | L2 | 0 |  |  |  | L3 ( | 0 | 0 | X | 1 | ) = | L3 ( 0 X 1 ) =
TOTAL UNBALANCED LOAD (1-PHASE) |  |  | 0 | VA | 0 | VA | 0 | VA |  |  |  | L3 | 0
[12 empty] | 0 | 0 | 0
|  |  | 0 | A | 0 | A | 0 | A |  |  |  | 3-PHASE DELTA |  | 0 | 0
LINE AMPS BALANCED (1-PHASE) |  |  | 0 | A | 0 | A | 0 | A |  |  |  | LOAD ERROR
LINE AMPS UNBALANCED (1-PHASE) |  |  | 0 | A | 0 | A | 0 | A |  |  |  | 0 | [10 empty] | 2000 | 3750 |  | 2500 |  | 2000
TOTALS |  |  | 0 | A | 0 | A | 0 | A
ADJUSTMENT FACTOR |  |  | 0 | A | 0 | A | 0 | A |  |  |  | 0 | [11 empty] | 2000 |  | 2000 |  | 2000
TOTAL DESIGN LOAD |  |  | 0 | A | 0 | A | 0 | A | [8 empty] | RECEPTACLE | L1 | L2 | L3 | TOTAL
[12 empty] | 0 |  |  |  |  | DIVERSITY | 0 | 0 |  | 0 |  |  | 1750 |  | 500 |  | 0
VOLTAGE DROP CALCULATIONS
|  | Single Phase | ( 2 X 50' L X 0.8080 R X 0.0 A ÷ 1,000 ) = 0.0 VD | [8 empty] | 99
|  | Voltage Drop % | ( 0.0 VD ÷ 240 V X 100 ) = 0.0 % VD
FAULT CURRENT CALCULATIONS
Available Fault Current at Starting Point (( 15,304 AFC X 1.00 UA ) + 0 MC ) = 15,304 AFC
Conductor Factor CF - Formula ( 2 X 50 L X 15,304 AFC ) ÷ ( 1,482 C X 1 N X 240 V ) = 4.303 CF
|  | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 4.303 CF ) = 0.189 CM | [9 empty] | MAX LINE AMPS | 0
Conductor Let-Through Current CLC - Formula ( 15,304 AFC X 0.189 CM ) = 2,892 CLC
[12 empty] | L1 | 0
[12 empty] | L2 | 0
[12 empty] | L3 | 0
[12 empty] | MAX WATTS | 0
[12 empty] | HARMONIC LOAD | 0
[12 empty] | TOTAL LOAD | 0
[12 empty] | HARMONIC % | 0
A - Amps |  |  | N - Number of Conductors Per Phase
AFC - Available Fault Current |  |  | R - Resistance | [9 empty] | ( | Harmonic Load | 0 | VA ÷ | Connected Load | 0 | VA ) X 100 = | 0 | % | ( Harmonic Load 0 VA ÷ Connected Load 0 VA ) X 100 = 0 %
C - Conductor Constant |  |  | UA - Utility Adjustment 1.1
CF - Conductor Factor |  |  | V - Voltage
CLC - Conductor Let-Through Current |  |  | VA - Volt Amps | [8 empty] | 0
CM - Conductor Multiplier |  |  | VD - Voltage Drop | [8 empty] | 0
L - Length of Conductor | [11 empty] | 0
MC - Motor Contribution | [11 empty] | 5
Prepared With Residential 1-Line 2008 Software - Copyright Durand & Associates
[12 empty] | 5 |  | 2 | 3 | 4 | 5 | 6 | 7
[12 empty] | A - Amps |  | A - Amps | A - Amps | A - Amps | A - Amps | %Z - Transformer Impedance Nameplate %Z | %Z - Transformer Impedance Nameplate %Z
[12 empty] | AFC - Available Fault Current |  | VA - Volt Amps | L - Length of Conductor | AFC - Available Fault Current | AFC - Available Fault Current | A - Amps | A - Amps
[12 empty] | C - Conductor Constant |  |  | R - Resistance | C - Conductor Constant | C - Conductor Constant | AFC - Available Fault Current | AFC - Available Fault Current
[12 empty] | CF - Conductor Factor |  |  | V - Voltage | CF - Conductor Factor | CF - Conductor Factor | C - Conductor Constant | C - Conductor Constant
[12 empty] | CLC - Conductor Let-Through Current |  |  | VA - Volt Amps | CLC - Conductor Let-Through Current | CLC - Conductor Let-Through Current | CF - Conductor Factor | CF - Conductor Factor
[12 empty] | CM - Conductor Multiplier |  |  | VD - Voltage Drop | CM - Conductor Multiplier | CM - Conductor Multiplier | CLC - Conductor Let-Through Current | CLC - Conductor Let-Through Current
[12 empty] | L - Length of Conductor |  |  |  | L - Length of Conductor | L - Length of Conductor | CM - Conductor Multiplier | CM - Conductor Multiplier
[12 empty] | MC - Motor Contribution |  |  |  | MC - Motor Contribution | MC - Motor Contribution | KVA - Kilovolt Amps | KVA - Kilovolt Amps
[12 empty] | N - Number of Conductors Per Phase |  |  |  | N - Number of Conductors Per Phase | N - Number of Conductors Per Phase | L - Length of Conductor | L - Length of Conductor
[12 empty] | R - Resistance |  |  |  | UA - Utility Adjustment 1.1 | R - Resistance | MC - Motor Contribution | MC - Motor Contribution
[12 empty] | UA - Utility Adjustment 1.1 |  |  |  | V - Voltage | UA - Utility Adjustment 1.1 | N - Number of Conductors Per Phase | N - Number of Conductors Per Phase
[12 empty] | V - Voltage |  |  |  | VA - Volt Amps | V - Voltage | PV - Primary Voltage | PV - Primary Voltage
[12 empty] | VA - Volt Amps |  |  |  |  | VA - Volt Amps | SV - Secondary Voltage | R - Resistance
[12 empty] | VD - Voltage Drop |  |  |  |  | VD - Voltage Drop | TF - Transformer Factor | SV - Secondary Voltage
[18 empty] | TLC - Transformer Let-Through Current | TF - Transformer Factor
[18 empty] | TM - Transformer Multiplier | TLC - Transformer Let-Through Current
[18 empty] | UA - Utility Adjustment 1.1 | TM - Transformer Multiplier
[18 empty] | V - Voltage | UA - Utility Adjustment 1.1
[18 empty] | VA - Volt Amps | V - Voltage
VA - Volt Amps
VD - Voltage Drop
aaaa

## Short No-Xmfr (hidden)
NO TRANSFORMER 3-PHASE Y
99
|  | Available Fault Current at Starting Point |  |  | (( | 15,304 | AFC x | 1 | UA ) + | 0 | MC ) = | 15304 | AFC
|  | Available Fault Current at Starting Point |  |  | (( | 15,304 | AFC X | 1.00 | UA ) + | 0 | MC ) = | 15,304 | AFC |  |  |  | Available Fault Current at Starting Point (( 15,304 AFC X 1.00 UA ) + 0 MC ) = 15,304 AFC
15,304 AFC
[14 empty] | 0.75 | 3/4"
[14 empty] | 1 | 1" | [7 empty] | SER
|  | 0 | [11 empty] | 1.25 | 1 1/4"
[14 empty] | 1.5 | 1 1/2" | [6 empty] | GENERAL | 0 | 0
[14 empty] | 2 | 2" | [6 empty] | RIGID | 0 | 0
[14 empty] | 2.5 | 2 1/2" | [6 empty] | EMT | 1 | 0
[14 empty] | 3 | 3" | [6 empty] | IMC | 0 | 0
[14 empty] | 3.5 | 3 1/2" | [6 empty] | PVC-40 | 0 | 0
[14 empty] | 4 | 4" | [6 empty] | RIGID/PVC | 0 | 0
[22 empty] | FLEX | 0 | 0
[22 empty] | LT-FLEX | 0 | 0
| Step 4 - Conductor Factor CF - Formula | [20 empty] | STELL=1 PLASTIC=2 | 5 | 0
| Three Phase | [20 empty] | CU=1 AL=2 | 1 | 2
Conductor Factor CF - Formula | ( | 2 | x | 50 | L x | 15304 | AFC ) ÷ ( | 1482 | C x | 1 | N x | 240 | V ) = | 4.303 |  | CF | Print
Conductor Factor CF - Formula | ( | 2 | X | 50 | L X | 15,304 | AFC ) ÷ ( | 1,482 | C X | 1 | N X | 240 | V ) = | 4.303 |  | CF | Conductor Factor CF - Formula ( 2 X 50 L X 15,304 AFC ) ÷ ( 1,482 C X 1 N X 240 V ) = 4.303 CF |  |  |  |  | TOTAL | 6 | 2
Step 5 - Conductor Multiplier CM - Formula
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 4.303 | CF ) = | 0.189 | CM | [7 empty] | Print
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | 4.303 | CF ) = | 0.189 | CM | [7 empty] | Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 4.303 CF ) = 0.189 CM
6
Step 6 - Conductor Let-Through Current CLC - Formula
Conductor Let-Through Current CLC - Formula | ( | 15304 | AFC X | 0.189 | CM ) = | 2892.456 | CLC | [9 empty] | Print |  |  |  |  | 6 |  | 1 | 2 | 3 | 4 | 5 | 6
Conductor Let-Through Current CLC - Formula | ( | 15,304 | AFC X | 0.189 | CM ) = | 2,892 | CLC |  |  | 2,892 CLC | [6 empty] | Conductor Let-Through Current CLC - Formula ( 15,304 AFC X 0.189 CM ) = 2,892 CLC |  |  |  |  | SER-ROMEX | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit | SER-ROMEX | SER-ROMEX
[22 empty] | CABLE |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | CABLE | CABLE
|  |  | Conductor Let-Through Current CLC - Formula ( 15,304 AFC X 0.189 CM ) = 2,892 CLC | [14 empty] | C7 | #6 | 5 |  | AL |  | Cables CU | Cables CU | Cables AL | Cables AL | CU | AL
[21 empty] | 1 | 237 | #14 | 389 | 389 | 237 | 237 | 389 | 237
[21 empty] | 2 | 376 | #12 | 617 | 617 | 376 | 376 | 617 | 376
[6 empty] | 2.9 | K |  |  | 2.9K | [10 empty] | 3 | 599 | #10 | 981 | 982 | 599 | 599 | 982 | 599
[21 empty] | 4 | 952 | #8 | 1557 | 1559 | 951 | 952 | 1560 | 952
[21 empty] | 5 | 1482 | #6 | 2425 | 2430 | 1481 | 1482 | 2433 | 1482
[21 empty] | 6 | 2353 | #4 | 3806 | 3826 | 2346 | 2350 | 3838 | 2353
[21 empty] | 7 | 2966 | #3 | 4774 | 4811 | 2952 | 2961 | 4833 | 2966
[21 empty] | 8 | 3740 | #2 | 5907 | 6044 | 3713 | 3730 | 6087 | 3740
[20 empty] | 5 | 9 | 4699 | #1 | 7293 | 7493 | 4645 | 4678 | 7579 | 4699
[21 empty] | 10 | 5876 | #1/0 | 8925 | 9317 | 5777 | 5838 | 9473 | 5876
[21 empty] | 11 | 7373 | #2/0 | 10755 | 11424 | 7187 | 7301 | 11703 | 7373
[21 empty] | 12 | 9243 | #3/0 | 12844 | 13923 | 8826 | 9110 | 14410 | 9243
[21 empty] | 13 | 11409 | #4/0 | 15082 | 16673 | 10741 | 11174 | 17438 | 11409
[21 empty] | 14 | 13236 | #250 | 16483 | 18594 | 12122 | 12862 | 19779 | 13236
[21 empty] | 15 | 15495 | #300 | 18177 | 20868 | 13910 | 14923 | 22525 | 15495
[21 empty] | 16 | 17635 | #350 | 19704 | 22737 | 15484 | 16813 | 24904 | 17635
[21 empty] | 17 | 19588 | #400 | 20566 | 24297 | 16671 | 18506 | 26916 | 19588
[21 empty] | 18 | 23018 | #500 | 22185 | 26706 | 18756 | 21391 | 30096 | 23018
[21 empty] | 1482 | #6

## Short Primary (hidden)
NO TRANSFORMER 3-PHASE Y
|  | Available Fault Current at Starting Point |  |  | (( | 0 | AFC x | 0 | UA ) + | 0 | MC ) = | 0 | AFC
|  | Available Fault Current at Starting Point |  |  | (( | 0 | AFC X | 0.00 | UA ) + | 0 | MC ) = | 0 | AFC |  |  |  | Available Fault Current at Starting Point (( 0 AFC X 0.00 UA ) + 0 MC ) = 0 AFC
0 AFC
[14 empty] | 0.75 | 3/4"
[14 empty] | 1 | 1"
[14 empty] | 1.25 | 1 1/4"
[14 empty] | 1.5 | 1 1/2" | [6 empty] | GENERAL | 0 | 0
[14 empty] | 2 | 2" | [6 empty] | RIGID | 0 | 0
[14 empty] | 2.5 | 2 1/2" | [6 empty] | EMT | 1 | 0
[14 empty] | 3 | 3" | [6 empty] | IMC | 0 | 0
[14 empty] | 3.5 | 3 1/2" | [6 empty] | PVC-40 | 0 | 0
[14 empty] | 4 | 4" | [6 empty] | RIGID/PVC | 0 | 0
[22 empty] | FLEX | 0 | 0
[22 empty] | LT-FLEX | 0 | 0
| Step 4 - Conductor Factor CF - Formula | [20 empty] | STELL=1 PLASTIC=2 | 1 | 0
| Three Phase | [20 empty] | CU=1 AL=2 | 2 | 2
Conductor Factor CF - Formula | ( | 2 | x | 0 | L x | 0 | AFC ) ÷ ( | 0 | C x | #N/A | N x | 240 | PV ) = | #N/A |  | CF | Print
Conductor Factor CF - Formula | ( | 2 | X | 0 | L X | 0 | AFC ) ÷ ( | 0 | C X | #N/A | N X | 240 | PV ) = | #N/A |  | CF | #N/A |  |  |  |  | TOTAL | 3 | 2
Step 5 - Conductor Multiplier CM - Formula
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #N/A | CF ) = | #N/A | CM | [7 empty] | Print
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #N/A | CF ) = | #N/A | CM | [7 empty] | #N/A
2
Step 6 - Conductor Let-Through Current CLC - Formula
Conductor Let-Through Current CLC - Formula | ( | 0 | AFC X | #N/A | CM ) = | #N/A | CLC | [9 empty] | Print |  |  |  |  | 2 |  | 1 | 2 | 3 | 4
Conductor Let-Through Current CLC - Formula | ( | 0 | AFC X | #N/A | CM ) = | #N/A | CLC |  |  | #N/A | [6 empty] | #N/A |  |  |  |  | Nonmagnetic Conduit | C VALUES | Steel Conduit | Nonmagnetic Conduit | Steel Conduit | Nonmagnetic Conduit
[22 empty] | 3 or 4 Single |  | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single | 3 or 4 Single
|  |  | #N/A | [14 empty] | C7 | #N/A | #N/A |  | Cables CU |  | Cables CU | Cables CU | Cables AL | Cables AL
[21 empty] | 1 | 389 | #14 | 389 | 389 | 237 | 237
[21 empty] | 2 | 617 | #12 | 617 | 617 | 376 | 376
[21 empty] | 3 | 982 | #10 | 981 | 982 | 599 | 599
[21 empty] | 4 | 1559 | #8 | 1557 | 1559 | 951 | 952
[21 empty] | 5 | 2430 | #6 | 2425 | 2430 | 1481 | 1482
[21 empty] | 6 | 3826 | #4 | 3806 | 3826 | 2346 | 2350
[21 empty] | 7 | 4811 | #3 | 4774 | 4811 | 2952 | 2961
[21 empty] | 8 | 6044 | #2 | 5907 | 6044 | 3713 | 3730
[20 empty] | #N/A | 9 | 7493 | #1 | 7293 | 7493 | 4645 | 4678
[21 empty] | 10 | 9317 | #1/0 | 8925 | 9317 | 5777 | 5838
[21 empty] | 11 | 11424 | #2/0 | 10755 | 11424 | 7187 | 7301
[21 empty] | 12 | 13923 | #3/0 | 12844 | 13923 | 8826 | 9110
[21 empty] | 13 | 16673 | #4/0 | 15082 | 16673 | 10741 | 11174
[21 empty] | 14 | 18594 | #250 | 16483 | 18594 | 12122 | 12862
[21 empty] | 15 | 20868 | #300 | 18177 | 20868 | 13910 | 14923
[21 empty] | 16 | 22737 | #350 | 19704 | 22737 | 15484 | 16813
[21 empty] | 17 | 24297 | #400 | 20566 | 24297 | 16671 | 18506
[21 empty] | 18 | 26706 | #500 | 22185 | 26706 | 18756 | 21391
[21 empty] | 0 | 0

## Short With Xmfr (hidden)
|  | Available Fault Current at Starting Point |  |  |  | #N/A | AFC
|  | Available Fault Current at Starting Point |  |  |  | #N/A | AFC |  |  | #N/A | [7 empty] | #N/A |  |  |  | 4
Step 4 - Calculated Factor F
| Three Phase | [20 empty] | 4 |  | 2 |  | 3 |  | 4 |  | 5 | 10
Conductor Factor CF - Formula | ( | 2 | x | 50 | L x | #N/A | TLC ) ÷ ( | 1481 | C x | 1 | N x | 240 | SV ) = | #N/A |  | CF | Print |  | EMT | 1 |  | Steel Conduit | C VALUES | Steel Conduit | Steel Conduit | Nonmagnetic Conduit | Nonmagnetic Conduit | Steel Conduit | Steel Conduit | Nonmagnetic Conduit | Nonmagnetic Conduit
Conductor Factor CF - Formula | ( | 2.000 | x | 50 | L x | #N/A | TLC ) ÷ ( | 1,481 | C x | 1 | N x | 240 | SV ) = | #N/A |  | CF | #N/A |  | AL | 3 |  | 3 or 4 Single |  | 3 or 4 Single | 3-Conductor | 3 or 4 Single | 3-Conductor | 3 or 4 Single | 3-Conductor | 3 or 4 Single | 3-Conductor
[22 empty] | Cables AL |  | Cables CU | Cables CU | Cables CU | Cables CU | Cables AL | Cables AL | Cables AL | Cables AL
| Step 5 - Calculate M | [18 empty] | 4 | 1 | 237 | #14 | 389 | 389 | 389 | 389 | 237 | 237 | 237 | 237
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #N/A | CF ) = | #N/A | CM | [7 empty] | Print |  |  |  | 2 | 376 | #12 | 617 | 617 | 617 | 617 | 376 | 376 | 376 | 376
Conductor Multiplier CM - Formula | ( | 1 | ) ÷ ( | 1 | + | #N/A | CF ) = | #N/A | CM | [7 empty] | #N/A |  |  |  | 3 | 599 | #10 | 981 | 982 | 982 | 982 | 599 | 599 | 599 | 599
[21 empty] | 4 | 951 | #8 | 1557 | 1559 | 1559 | 1560 | 951 | 952 | 952 | 952
| Step 6 - Available Short Circuit (RMS Symmetrical) | [17 empty] | WIRE CODE | 5 | 5 | 1481 | #6 | 2425 | 2431 | 2430 | 2433 | 1481 | 1482 | 1482 | 1482
Conductor Let-Through Current CLC - Formula | ( | #N/A | TLC x | #N/A | CM ) = | #N/A | CLC | [9 empty] | Print |  |  |  | 6 | 2346 | #4 | 3806 | 3830 | 3826 | 3838 | 2346 | 2351 | 2350 | 2353
Conductor Let-Through Current CLC - Formula | ( | #N/A | TLC x | #N/A | CM ) = | #N/A | CLC |  |  | #N/A | [6 empty] | #N/A |  |  |  | 7 | 2952 | #3 | 4774 | 4820 | 4811 | 4833 | 2952 | 2963 | 2961 | 2966
[21 empty] | 8 | 3713 | #2 | 5907 | 5989 | 6044 | 6087 | 3713 | 3734 | 3730 | 3740
|  |  | #N/A | [17 empty] | 9 | 4645 | #1 | 7293 | 7454 | 7493 | 7579 | 4645 | 4686 | 4678 | 4699
[21 empty] | 10 | 5777 | #1/0 | 8925 | 9210 | 9317 | 9473 | 5777 | 5852 | 5838 | 5876
| SECONDARY TRANSFORMER | [19 empty] | 11 | 7187 | #2/0 | 10755 | 11245 | 11424 | 11703 | 7187 | 7327 | 7301 | 7373
[21 empty] | 12 | 8826 | #3/0 | 12844 | 13656 | 13923 | 14410 | 8826 | 9077 | 9110 | 9243
| Step A Calculate TF | [19 empty] | 13 | 10741 | #4/0 | 15082 | 16392 | 16673 | 17483 | 10741 | 11185 | 11174 | 11409
| ( | #N/A | AFC x | 240 | PV x | 2 | x | 2,892 | %Z ) ÷ ( | 100000 | x | 0 | KVA ) = | #N/A | [6 empty] | 14 | 12122 | 250 MCM | 16483 | 18311 | 18594 | 19779 | 12122 | 12797 | 12862 | 13236
| ( | #N/A | AFC x | 240 | PV x | 2.000 | x | 2892.0 | %Z ) ÷ ( | 100,000 | x | 0.0 | KVA ) = | #N/A | TF |  | Calculate TF | #N/A |  |  | 15 | 13910 | 300 MCM | 18177 | 20617 | 20868 | 22525 | 13910 | 14917 | 14923 | 15495
| Step B Calculate tM | [9 empty] | < | KVA | < 0.0 KVA | [7 empty] | 16 | 15484 | 350 MCM | 19704 | 22646 | 22737 | 24904 | 15484 | 16795 | 16813 | 17635
| ( | 1 | ) / ( | 1 | + | #N/A | TF ) = | #N/A | TM | [11 empty] | 17 | 16671 | 400 MCM | 20566 | 24253 | 24297 | 26916 | 16671 | 18462 | 18506 | 19588
| ( | 1 | ) / ( | 1 | + | #N/A | TF ) = | #N/A | TM | [7 empty] | Calculate TM | #N/A |  |  | 18 | 18756 | 500 MCM | 22185 | 26980 | 26706 | 30096 | 18756 | 21395 | 21391 | 23018
| Step C Calculate TLC | [19 empty] | 19 | 20093 | 600 MCM | 22965 | 28752 | 28033 | 32154 | 20093 | 23633 | 23451 | 25708
| (((( | 240 | PV ÷ | 240 | SV ) ÷ ( | #N/A | TM x | #N/A | AFC )) x | 0 | UA ) + | 0 | MC ) = | #N/A | TLC | [5 empty] | 20 | 21766 | 750 MCM | 24137 | 31051 | 29735 | 34605 | 21766 | 26432 | 25976 | 29036
| (((( | 240 | PV ÷ | 240 | SV ) ÷ ( | #N/A | TM x | #N/A | AFC )) x | 0.0 | UA ) + | 0 | MC ) = | #N/A | TLC |  | Calculate TLC | #N/A |  |  | 21 | 23478 | 1000 MCM | 25278 | 33864 | 31491 | 37197 | 23478 | 29865 | 28779 | 32938
[10 empty] | #N/A | TLC |  | #N/A
[21 empty] | 1481 | #6
÷
1481
| (((( | 480 | PV ÷ | 208 | SV ) ÷ ( | 0.282 | TM x | 46,000 | AFC )) x | ua | UA ) + | mc | =
| %Z | - Transformer Impedance Value Nameplate %Z
| AFC | - Available Fault Current
| C | - Conductor Constant
| CF | - Conductor Factor
| CLC | - Conductor Let-Through Current | [23 empty] | 0 | 4
| CM | - Conductor Multiplier | [20 empty] | 50
| KVA | - Kilovolt Amps | [20 empty] | Steel Conduit |  |  | 1 | #14 Cable CU | #14 Cable CU | #14 Cable AL | AL | #14 Cable AL AL
| L | - Length of Conductor | [20 empty] | 1 Conductor(s) Per Phase |  |  | 2 | #12 Cable CU | #12 Cable CU | #12 Cable AL | AL
| MC | - Motor Short-Circuit Contribution | [20 empty] | #N/A |  |  | 3 | #10 Cable CU | #10 Cable CU | #10 Cable AL | AL
| N | - Number of Conductors Per Phase | [23 empty] | 4 | #8 Cable CU | #8 Cable CU | #8 Cable AL | AL
| PV | - Primary Voltage | [23 empty] | 5 | #6 Cable CU | #6 Cable CU | #6 Cable AL | AL
| SV | - Secondary Voltage | [23 empty] | 6 | #4 Cable CU | #4 Cable CU | #4 Cable AL | AL
| TF | - Transformer Factor | [23 empty] | 7 | #3 Cable CU | #3 Cable CU | #3 Cable AL | AL
| TLC | - Transformer Let-Through Current | [19 empty] | 1 | 1 Conductor(s) Per Phase |  |  | 8 | #2 Cable CU | #2 Cable CU | #2 Cable AL | AL
| TM | - Transformer Multiplier | [19 empty] | 2 | 2 Conductor(s) Per Phase |  |  | 9 | #1 Cable CU | #1 Cable CU | #1 Cable AL | AL
| UA | - Utility Adjustment 1.1 ( Voltages May Vary 10% ) | [19 empty] | 3 | 3 Conductor(s) Per Phase |  |  | 10 | #1/0 Cable CU | #1/0 Cable CU | #1/0 Cable AL | AL
[22 empty] | 4 | 4 Conductor(s) Per Phase |  |  | 11 | #2/0 Cable CU | #2/0 Cable CU | #2/0 Cable AL | AL
[22 empty] | 5 | 5 Conductor(s) Per Phase |  |  | 12 | #3/0 Cable CU | #3/0 Cable CU | #3/0 Cable AL | AL
[22 empty] | 6 | 6 Conductor(s) Per Phase |  |  | 13 | #4/0 Cable CU | #4/0 Cable CU | #4/0 Cable AL | AL
[22 empty] | 7 | 7 Conductor(s) Per Phase |  |  | 14 | 250 MCM Cable CU | 250 MCM Cable CU | 250 MCM Cable AL | AL
[22 empty] | 8 | 8 Conductor(s) Per Phase |  |  | 15 | 300 MCM Cable CU | 300 MCM Cable CU | 300 MCM Cable AL | AL
[22 empty] | 9 | 9 Conductor(s) Per Phase |  |  | 16 | 350 MCM Cable CU | 350 MCM Cable CU | 350 MCM Cable AL | AL
[22 empty] | 10 | 10 Conductor(s) Per Phase |  |  | 17 | 400 MCM Cable CU | 400 MCM Cable CU | 400 MCM Cable AL | AL
[22 empty] | 11 | 11 Conductor(s) Per Phase |  |  | 18 | 500 MCM Cable CU | 500 MCM Cable CU | 500 MCM Cable AL | AL
[22 empty] | 12 | 12 Conductor(s) Per Phase |  |  | 19 | 600 MCM Cable CU | 600 MCM Cable CU | 600 MCM Cable AL | AL
[22 empty] | 13 | 13 Conductor(s) Per Phase |  |  | 20 | 750 MCM Cable CU | 750 MCM Cable CU | 750 MCM Cable AL | AL
[22 empty] | 14 | 14 Conductor(s) Per Phase |  |  | 21 | 1000 MCM Cable CU | 1000 MCM Cable CU | 1000 MCM Cable AL | AL
[22 empty] | 15 | 15 Conductor(s) Per Phase
[22 empty] | 16 | 16 Conductor(s) Per Phase |  |  | #N/A
[22 empty] | 17 | 17 Conductor(s) Per Phase
[22 empty] | 18 | 18 Conductor(s) Per Phase
[22 empty] | 19 | 19 Conductor(s) Per Phase
[22 empty] | 20 | 20 Conductor(s) Per Phase
1 Conductor(s) Per Phase

## S-Output-Input (hidden)
OUTPUT
| PANEL | FED FROM | NUMBER OF | HIGH | LOW | PHASE | HIGH LEG | NEUTRAL | GROUND | GROUND | WIRE | WIRE | WIRE | WIRE | CONDUIT | MINIMUM | KITCHEN | % FACTOR | MAIN | AFC | AFC AT | UTILITY | AFC AT | NUMBER | CONDUIT | CONDUIT | WIRE | WIRE | WIRE | WIRE | WIRE | WIRE | NEUTRAL | NEUTRAL | GROUND | GROUND | 1-PHASE | 1-PHASE | 3-PHASE Y | 3-PHASE Y | 3-PHASE D | 3-PHASE D | 3-PHASE D | 3-PHASE D | GENERAL | GENERAL | GENERAL | RECEPTACLE | RECEPTACLE | RECEPTACLE | CONTINUOUS | CONTINUOUS | CONTINUOUS | MOTOR | MOTOR | MOTOR | LARGEST | LARGEST | LARGEST | KITCHEN | KITCHEN | KITCHEN
| NAME |  | CIRCUITS | VOLTAGE | VOLTAGE |  | SIZE | SIZE | BUS | WIRE | TYPE | CA/AL | TEMP | LENGTH | TYPE | AMPS | LOADS |  | BREAKER | CALC | START | VOLTAGE | TRANS | OF | SIZE | SIZE | SIZE | CODE | SIZE | CODE | SIZE | CODE | SIZE | CODE | SIZE | WIRE | L1 & L3 | L1 & L3 | L1 L2 L3 | L1 L2 L3 | L2 | L2 | L1 & L3 | L1 & L3 | LOAD | LOAD | LOAD | LOADS | LOADS | LOADS | LOAD | LOAD | LOAD | LOAD | LOAD | LOAD | MOTOR | MOTOR | MOTOR | LOAD | LOAD | LOAD
| TEXT | VALUE | VALUE | [5 empty] | Y/N | Y/N | [8 empty] | Y/N | METHOD | POINT | ADJUST |  | CONDUITS |  | CODE | L1 | L1 | L2 | L2 | L3 | L3 |  |  |  | CODE | VD | % VD | VD | % VD | VD | % VD | VD | % VD | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3 | L1 | L2 | L3
| HP2 | CP1 | 84 | 240 | 120 | 1 | 0 | 0 | 0 | Y | THHN | AL | 75 | 50 | EMT | 0 | 0 | 0 | Y | 0 | 15,304 | 1 | 0 | 1 | 3/4'' | 0.75 | #6 | 5 | #6 | 5 | #6 | #6 | #6 | 5 | #8 | 4 | 0.0 VD | 0.0 % VD | 0.0 VD | 0.0 % VD | 0.0 VD | 0.0 % VD | 0.0 VD | 0.0 % VD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SUB PANEL | NONE
IMPUT
AFC
| AT MIAN |  |  |  | HP2
15,304
HP2
TRANS Y/N
SPACE
| # OF CONDUITS | 0
-
| CONDUIT SIZE | 0
SPACE
| CONDUIT TYPE | 0
WIRE 1
WIRE 2
0 | AFC TRANS | 0
K
AFC TRANS
| VOTAGE DROP | #N/A
| PRIMARY | % VD
| TRANS KVA | 0
KVA
| TRANS GND WIRE | 0
GND
| TLC | #N/A
K
SECONDARY
SPACE
| # OF CONDUITS | 1
-
| CABLE TYPE | SER CABLE
SPACE
CONDUIT TYPE
50
'
|  | CONDUIT |  | CABLE |  | 50'
| WIRE 1 |  |  | 3-#6 AL |  | 3-#6 AL
| WIRE 2 |  |  | 1-#6 GND |  | 1-#6 GND
WIRE 3
WIRE 4
| CLC | 2.9
K
| VOTAGE DROP | 0.0
| PRIMARY | % VD
SUB PANEL
| NAME | HP2

## S-Directory (hidden)
MASTER
CIRCUIT DIRECTORY PANEL |  |  | HP2 |  | ERROR
THIS SUB PANEL IS NOT BEING USED |  |  |  |  | 999 | 84
CIR | DESCRIPTION | L1 | DESCRIPTION | CIR
1 |  | L2 | LIGHTS | 2 | 0
3 |  | L1 | LIGHTS | 4 | 0
5 |  | L2 | LIGHTS | 6 | 0
7 |  | L1 | LIGHTS | 8 | 0
9 |  | L2 | LIGHTS | 10 | 0
11 | PINK CELLS ARE | L1 | LIGHTS | 12 | 0
13 | PROTECTED IN DEMO | L2 | LIGHTS | 14 | 0
15 |  | L1 | LIGHTS | 16 | 0
17 |  | L2 | LIGHTS | 18 | 0
19 |  | L1 | LIGHTS | 20 | 0
21 |  | L2 | LIGHTS | 22 | 0
23 |  | L1 | LIGHTS | 24 | 0
25 |  | L2 | LIGHTS | 26 | 0
27 |  | L1 |  | 28 | 0
29 |  | L2 |  | 30 | 0
31 |  | L1 |  | 32 | 0
33 |  | L2 |  | 34 | 0
35 |  | L1 |  | 36 | 0
37 |  | L2 |  | 38 | 0
39 |  | L1 |  | 40 | 0
41 |  | L2 |  | 42 | 0
43 |  | L1 |  | 44 | 0
45 |  | L2 |  | 46 | 0
47 |  | L1 |  | 48 | 0
49 |  | L2 |  | 50 | 0
51 |  | L1 |  | 52 | 0
53 |  | L2 |  | 54 | 0
55 |  | L1 |  | 56 | 0
57 |  | L2 |  | 58 | 0
59 |  | L1 |  | 60 | 0
61 |  | L2 |  | 62 | 0
63 |  | L1 |  | 64 | 0
65 |  | L2 |  | 66 | 0
67 |  | L1 |  | 68 | 0
69 |  | L2 |  | 70 | 0
71 |  | L1 |  | 72 | 0
73 |  | L2 |  | 74 | 0
75 |  | L1 |  | 76 | 0
77 |  | L2 |  | 78 | 0
79 |  | L1 |  | 80 | 0
81 |  | L2 |  | 82 | 0
83 |  | 0 |  | 84 | 0

## CopyPaste
NO COPY PASTE
Do not use the COPY and PASTE commands on this template as they can corrupt the file.
Each cell in this template has been formatted with error checking and performance codes. When
you copy a cell and use the PASTE command, these formats and performance codes are pasted
to the new location.
PASTE SPECIAL (Values Only)
To avoid corrupting the file use the COPY and the EDIT/PASTE SPECIAL command selecting
VALUES from the PASTE SPECIAL MENU.
Click on Values ------
Click OK ----------------

## CAD
CAD - Copying calculations and pasting in to your CAD program.
Step 1.
Using the mouse highlight the area you wish to copy.
VA
VA
VA
VA
VA
VA
VA
VA
Step 2.
Hold the SHIFT KEY down and use the mouse to select EDIT menu.
Step 3.
Select the COPY PICTURE command from the EDIT menu.
- - - - - Copy Picture
Step 4.
Select the "As shown when printed" and click OK.
Select
As shown when printed - - - -
Then click OK
Step 5.
Go to you CAD program and paste the graphic.
END