## Step 1
This is Step 1 and it will calculate the transformer let-through current.
Or you may manual enter available fault current.
| Project Name | Smioth Ranch
| Starting Point | Main Service
| Ending Point | Main Switch Board
| Select Method | Transformer Known AFC | 0 | 3
| Available Fault Current | 39425 | 0
| Transformer KVA | 300 | 0
| Phase | Three Phase | 0 |  | 1.732
| Primary Voltage | 480 | 0
| Transformer %Z Rating | 2 | 0
| Secondary Voltage | 208 | 0
* | Motor Short-Circuit Contribution | 0 | 0
** | Utility Voltage Adjustment | 1 | 0
* | Motor short-circuit contribution, if significant should
br added at all fault locations throughout the system.
A practicle estimate of short-circuit contribution is to
multiply the total motor full-load amps ( FLA ) by 4
Values of 4 to 6 are commonly accepted.
EXAMPLE ( 84 FLA x 4 ) = 336 AMPS
** | Utility voltages may vary +/- 10% for power. Therefore
| for worst case conditions enter 1.1 as the utility voltage adjustment. |  |  |  |  | Project Name - | Smioth Ranch | Project Name - Smioth Ranch
[6 empty] | Starting Point - | Main Service | Starting Point - Main Service
Math function in this DEMO have been disabled.
|  |  | 0 |  |  | Ending Point - | Main Switch Board | Ending Point - Main Switch Board
0

## Step 2
This is Step 2 and it will calculate the available short circuit current (RMS) symmetrical
Enter Conduit or Busway Length | 20 | [5 empty] | 0
Select One | [5 empty] | 0
3-SINGLE CONDUCTORS (Copper) Steel Conduit | 500 MCM | 1 | 0 | 0 | 1 | 1 | 0 | 0
1-THREE CONDUCTOR CABLE (Copper) Steel Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
3-SINGLE CONDUCTORS (Copper) Nomagnetic Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
1-THREE CONDUCTOR CABLE (Copper) Nomagnetic Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUSWAY (Copper) | No | 0 |  | 0 | 0 | 0 | 0 | 0
PLUG-IN BUSWAY (Copper) | No | 0 |  | 0 | 0 | 0 | 0 | 0
3-SINGLE CONDUCTORS (Aluminum) Steel Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
1-THREE CONDUCTOR CABLE (Aluminum) Steel Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
3-SINGLE CONDUCTORS (Aluminum) Nomagnetic Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
1-THREE CONDUCTOR CABLE (Aluminum) Nomagnetic Conduit | No | 0 | 0 | 0 | 0 | 0 | 0 | 0
BUSWAY (Aluminum) | No | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 1 |  |  |  | 1 | 0 | 0
Number of conductors Per Phase | 2 | 12 |  |  |  |  | 0
Math function in this DEMO have been disabled.
|  |  | MASTOR ERROR |  |  |  | 0
÷
[9 empty] | (((( | 480 | PV ÷ | 208 | SV ) ÷ ( | 0.282 | TM x | 46,000 | AFC )) x | ua | UA ) + | mc | =

## Printout
|  |  | Error Sheet 1 | 0
Point to Point Method of Short-Circuit Calculation ( Three Phase ) |  |  | Error Sheet 2 | 0
|  |  | sum | 0
|  |  | Auto/Manual | 3
Project Name - Smioth Ranch
Starting Point - Main Service
Ending Point - Main Switch Board
Step 1
Available Fault Current at Starting Point 39,425 AFC
Calculate TF ( 39,425 AFC x 480 PV x 1.732 x 2.0 %Z ) ÷ ( 100,000 x 300 KVA ) = 2.185 TF
Calculate TM ( 1 ) / ( 1 + 2.185 TF ) = 0.314 TM
Calculate TLC (((( 480 PV ÷ 208 SV ) ÷ ( 0.314 TM x 39,425 AFC )) x 1.0 UA ) + 0 MC ) = 28,568 TLC
Step 2
Conductor Factor CF - Formula ( 1.732 x 20 L x 28,568 TLC ) ÷ ( 22,185 C x 2 N x 208 SV ) = 0.107 CF
Conductor Multiplier CM - Formula ( 1 ) ÷ ( 1 + 0.107 CF ) = 0.903 CM
Conductor Let-Through Current CLC - Formula ( 28,568 TLC x 0.903 CM ) = 25,797 CLC
Start > | < | 39,425 AFC
Transformer
| \/\/\/\/\/\/\/ | < 300 KVA
/\/\/\/\/\/\/\
| < | 28,568 TLC
| < | 20
Steel Conduit
2 Conductor(s) Per Phase
500 MCM Cable CU
End > | < | 25,797 CLC
KEY
| %Z | - Transformer Impedance Value Nameplate %Z
| AFC | - Available Fault Current
| C | - Conductor Constant
| CF | - Conductor Factor
| CLC | - Conductor Let-Through Current
| CM | - Conductor Multiplier
| KVA | - Kilovolt Amps
| L | - Length of Conductor
| MC | - Motor Short-Circuit Contribution
| N | - Number of Conductors Per Phase
| PV | - Primary Voltage
| SV | - Secondary Voltage
| TF | - Transformer Factor
| TLC | - Transformer Let-Through Current
| TM | - Transformer Multiplier
| UA | - Utility Adjustment 1.1 ( Voltages May Vary 10% )
Prepared with Short-Circuit - Copyright Durand & Associates