## About
Electric Math
Version 1.2
Welcome to Motor Conductor Sizing Template
Use the tabs at the bottom to select input page.
This is a DEMO VERSION and the math
functions have been disabled

## Single Phase
SINGLE PHASE MOTORS |  |  |  |  | FLA SELECTION MODULE (Single Phase)
|  |  |  | ERROR | [7 empty] | CONDUCTOR SELECTION
VOLTAGE | 208 Volt | < User Entry | 208 | 0 |  |  | SINGLE PHASE MOTOR LOADS
HORSEPOWER | 3 HP | < User Entry | 3 HP | 0 | SELECTED | SELECTED | [5 empty] | COOPER WIRE SELECTION
WIRE CU? AL? | Aluminum | < User Entry | AL | 0 | FLA | 208V | HP | 115V | 200V | 208V | 230V | NEC 310.16
WIRE TEMP | 90 C | < User Entry | 90 | 0 | 0 | 2.4 | 0.16667 | 4.4 | 2.5 | 2.4 | 2.2
CONTINUOUS DUTY ( Y/N ) | No | < User Entry | No | 0 | 0 | 3.2 | 0.25 | 5.8 | 3.3 | 3.2 | 2.9 | AMPS | TEMP
|  |  |  | 0 | 0 | 4 | 0.33333 | 7.2 | 4.1 | 4 | 3.6 | 18.7 | 90 | SIZE | WIRE NO | 60 C | 75 C | 90 C
[5 empty] | 0 | 5.4 | 0.5 | 9.8 | 5.6 | 5.4 | 4.9 | 1e-05 | 15 | #14 | 1 | 15 | 15 | 15
[5 empty] | 0 | 7.6 | 0.75 | 13.8 | 7.9 | 7.6 | 6.9 | 15 | 20 | #12 | 2 | 20 | 20 | 20
FULL LOAD AMPS | 18.7 | < Program Generated |  |  | 0 | 8.8 | 1 | 16 | 9.2 | 8.8 | 8 | 20 | 30 | #10 | 3 | 30 | 30 | 30
WIRE SIZE | #12 | < Program Generated |  |  | 0 | 11 | 1.5 | 20 | 11.5 | 11 | 10 | 30 | 55 | #8 | 4 | 40 | 50 | 55
|  |  | 18.7 | AMPS | 0 | 13.2 | 2 | 24 | 13.8 | 13.2 | 12 | 55 | 75 | #6 | 5 | 55 | 65 | 75
|  |  | 0 |  | 18.7 | 18.7 | 3 | 34 | 19.6 | 18.7 | 17 | 75 | 95 | #4 | 6 | 70 | 85 | 95
|  |  | 18.7 | SIZE AMPS | 0 | 30.8 | 5 | 56 | 32.2 | 30.8 | 28 | 95 | 110 | #3 | 7 | 85 | 100 | 110
This is a DEMO VERSION and the |  |  |  |  | 0 | 44 | 7.5 | 80 | 46 | 44 | 40 | 110 | 130 | #2 | 8 | 95 | 115 | 130
math functions are disabled. |  |  |  |  | 0 | 55 | 10 | 100 | 57.5 | 55 | 50 | 130 | 150 | #1 | 9 | 110 | 130 | 150
[12 empty] | 150 | 170 | #1/0 | 10 | 125 | 150 | 170
|  |  | #12 | AL | 18.7 | FLA | [5 empty] | 170 | 195 | #2/0 | 11 | 145 | 175 | 195
[12 empty] | 195 | 225 | #3/0 | 12 | 165 | 200 | 225
[12 empty] | 225 | 260 | #4/0 | 13 | 195 | 230 | 260
[12 empty] | 260 | 290 | #250 | 14 | 215 | 255 | 290
[12 empty] | 290 | 320 | #300 | 15 | 240 | 285 | 320
[12 empty] | 320 | 350 | #350 | 16 | 260 | 310 | 350
[12 empty] | 350 | 380 | #400 | 17 | 280 | 335 | 380
[12 empty] | 380 | 430 | #500 | 18 | 320 | 380 | 430
[12 empty] | 430 | 475 | #600 | 19 | 355 | 420 | 475
[12 empty] | 475 | 520 | #700 | 20 | 385 | 460 | 520
[12 empty] | 520 | 535 | #750 | 21 | 400 | 475 | 535
OUTPUT
[12 empty] | 20 | WIRE AMPS CU
[12 empty] | #12 | WIRE SIZE CU
[12 empty] | 2 | WIRE NO
CONDUCTOR SELECTION
ALUMINUM WIRE SELECTION
NEC 310.16
[12 empty] | AMPS | TEMP
[12 empty] | 18.7 | 90 | SIZE | WIRE NO | 60 C | 75 C | 90 C
[12 empty] | 1e-05 | 20 | #12 | 2 | 20 | 20 | 20
[12 empty] | 20 | 30 | #10 | 3 | 25 | 30 | 30
[12 empty] | 30 | 45 | #8 | 4 | 30 | 40 | 45
[12 empty] | 45 | 60 | #6 | 5 | 40 | 50 | 60
[12 empty] | 60 | 75 | #4 | 6 | 55 | 65 | 75
[12 empty] | 75 | 100 | #2 | 8 | 75 | 90 | 100
[12 empty] | 100 | 115 | #1 | 9 | 85 | 100 | 115
[12 empty] | 115 | 135 | #1/0 | 10 | 100 | 120 | 135
[12 empty] | 135 | 150 | #2/0 | 11 | 115 | 135 | 150
[12 empty] | 150 | 175 | #3/0 | 12 | 130 | 155 | 175
[12 empty] | 175 | 205 | #4/0 | 13 | 150 | 180 | 205
[12 empty] | 205 | 230 | #250 | 14 | 170 | 205 | 230
[12 empty] | 230 | 255 | #300 | 15 | 190 | 230 | 255
[12 empty] | 255 | 280 | #350 | 16 | 210 | 250 | 280
[12 empty] | 280 | 305 | #400 | 17 | 225 | 270 | 305
[12 empty] | 305 | 350 | #500 | 18 | 260 | 310 | 350
[12 empty] | 350 | 385 | #600 | 19 | 285 | 340 | 385
[12 empty] | 385 | 420 | #700 | 20 | 310 | 375 | 420
[12 empty] | 420 | 435 | #750 | 21 | 320 | 385 | 435
OUTPUT
[12 empty] | 20 | WIRE AMPS AL
[12 empty] | #12 | WIRE SIZE AL
[12 empty] | 2 | WIRE NO

## Three Phase
THREE PHASE MOTORS |  |  |  |  | FLA SELECTION MODULE (Single Phase)
|  |  |  | ERROR | [9 empty] | CONDUCTOR SELECTION
VOLTAGE | 115 Volt | < User Entry | 115 | 0 |  |  | THREE PHASE MOTORS
HORSEPOWER | 2 HP | < User Entry | 2 HP | 0 | SELECTED | SELECTED | [7 empty] | COOPER WIRE SELECTION
WIRE CU? AL? | Copper | < User Entry | CU | 0 | FLA | 115V | HP | 115V | 200V | 208V | 230V | 460V | 575V | NEC 310.16
WIRE TEMP | 90 C | < User Entry | 90 | 0 | 0 | 4.4 | 0.5 | 4.4 | 2.5 | 2.4 | 2.2 | 1.1 | 0.9
CONTINUOUS DUTY ( Y/N ) | Yes | < User Entry | Yes | 0 | 0 | 6.4 | 0.75 | 6.4 | 3.7 | 3.5 | 3.2 | 1.6 | 1.3 | AMPS | TEMP
[5 empty] | 0 | 8.4 | 1 | 8.4 | 4.8 | 4.6 | 4.2 | 2.1 | 1.7 | 17 | 90 | SIZE | WIRE NO | 60 C | 75 C | 90 C
|  |  |  | 0 | 0 | 12 | 1.5 | 12 | 6.9 | 6.6 | 6 | 3 | 2.4 | 1e-05 | 15 | #14 | 1 | 15 | 15 | 15
|  |  |  | 0 | 13.6 | 13.6 | 2 | 13.6 | 7.8 | 7.5 | 6.8 | 3.4 | 2.7 | 15 | 20 | #12 | 2 | 20 | 20 | 20
|  | < Program Generated |  |  | 0 | -999999 | 3 | -999999 | 11 | 10.6 | 9.6 | 4.8 | 3.9 | 20 | 30 | #10 | 3 | 30 | 30 | 30
FULL LOAD AMPS | 13.6 | < Program Generated |  |  | 0 | -999999 | 5 | -999999 | 17.5 | 16.7 | 15.2 | 7.6 | 6.1 | 30 | 55 | #8 | 4 | 40 | 50 | 55
WIRE SIZE | #12 |  | 13.6 | AMPS | 0 | -999999 | 7.5 | -999999 | 25.3 | 24.2 | 22 | 11 | 9 | 55 | 75 | #6 | 5 | 55 | 65 | 75
|  |  | 3.4 |  | 0 | -999999 | 10 | -999999 | 32.2 | 30.8 | 28 | 14 | 11 | 75 | 95 | #4 | 6 | 70 | 85 | 95
|  |  | 17 | SIZE AMPS | 0 | -999999 | 15 | -999999 | 48.3 | 46.2 | 42 | 21 | 17 | 95 | 110 | #3 | 7 | 85 | 100 | 110
This is a DEMO VERSION and the |  |  |  |  | 0 | -999999 | 20 | -999999 | 62.1 | 59.4 | 54 | 27 | 22 | 110 | 130 | #2 | 8 | 95 | 115 | 130
math functions are disabled. |  |  |  |  | 0 | -999999 | 25 | -999999 | 78.2 | 74.8 | 68 | 34 | 27 | 130 | 150 | #1 | 9 | 110 | 130 | 150
|  |  | #12 | CU | 0 | -999999 | 30 | -999999 | 92 | 88 | 80 | 40 | 32 | 150 | 170 | #1/0 | 10 | 125 | 150 | 170
[5 empty] | 0 | -999999 | 40 | -999999 | 120 | 114 | 104 | 52 | 41 | 170 | 195 | #2/0 | 11 | 145 | 175 | 195
[5 empty] | 0 | -999999 | 50 | -999999 | 150 | 143 | 130 | 65 | 52 | 195 | 225 | #3/0 | 12 | 165 | 200 | 225
[5 empty] | 0 | -999999 | 60 | -999999 | 177 | 169 | 154 | 77 | 62 | 225 | 260 | #4/0 | 13 | 195 | 230 | 260
[5 empty] | 0 | -999999 | 75 | -999999 | 221 | 211 | 192 | 96 | 77 | 260 | 290 | #250 | 14 | 215 | 255 | 290
[5 empty] | 0 | -999999 | 100 | -999999 | 285 | 273 | 248 | 124 | 99 | 290 | 320 | #300 | 15 | 240 | 285 | 320
[5 empty] | 0 | -999999 | 125 | -999999 | 359 | 343 | 312 | 156 | 125 | 320 | 350 | #350 | 16 | 260 | 310 | 350
[14 empty] | 350 | 380 | #400 | 17 | 280 | 335 | 380
[5 empty] | 13.6 | FLA | [7 empty] | 380 | 430 | #500 | 18 | 320 | 380 | 430
[14 empty] | 430 | 475 | #600 | 19 | 355 | 420 | 475
[14 empty] | 475 | 520 | #700 | 20 | 385 | 460 | 520
[14 empty] | 520 | 535 | #750 | 21 | 400 | 475 | 535
OUTPUT
[14 empty] | 20 | WIRE AMPS CU
[14 empty] | #12 | WIRE SIZE CU
[14 empty] | 2 | WIRE NO
CONDUCTOR SELECTION
ALUMINUM WIRE SELECTION
NEC 310.16
[14 empty] | AMPS | TEMP
[14 empty] | 17 | 90 | SIZE | WIRE NO | 60 C | 75 C | 90 C
[14 empty] | 1e-05 | 20 | #12 | 2 | 20 | 20 | 20
[14 empty] | 20 | 30 | #10 | 3 | 25 | 30 | 30
[14 empty] | 30 | 45 | #8 | 4 | 30 | 40 | 45
[14 empty] | 45 | 60 | #6 | 5 | 40 | 50 | 60
[14 empty] | 60 | 75 | #4 | 6 | 55 | 65 | 75
[14 empty] | 75 | 100 | #2 | 8 | 75 | 90 | 100
[14 empty] | 100 | 115 | #1 | 9 | 85 | 100 | 115
[14 empty] | 115 | 135 | #1/0 | 10 | 100 | 120 | 135
[14 empty] | 135 | 150 | #2/0 | 11 | 115 | 135 | 150
[14 empty] | 150 | 175 | #3/0 | 12 | 130 | 155 | 175
[14 empty] | 175 | 205 | #4/0 | 13 | 150 | 180 | 205
[14 empty] | 205 | 230 | #250 | 14 | 170 | 205 | 230
[14 empty] | 230 | 255 | #300 | 15 | 190 | 230 | 255
[14 empty] | 255 | 280 | #350 | 16 | 210 | 250 | 280
[14 empty] | 280 | 305 | #400 | 17 | 225 | 270 | 305
[14 empty] | 305 | 350 | #500 | 18 | 260 | 310 | 350
[14 empty] | 350 | 385 | #600 | 19 | 285 | 340 | 385
[14 empty] | 385 | 420 | #700 | 20 | 310 | 375 | 420
[14 empty] | 420 | 435 | #750 | 21 | 320 | 385 | 435
OUTPUT
[14 empty] | 20 | WIRE AMPS AL
[14 empty] | #12 | WIRE SIZE AL
[14 empty] | 2 | WIRE NO